## Summary
Parameter | Value
OPTIMIZATION RESULTS
Total System Cost | 5670.67 EUR/a
Number of Scenarios | 3
Number of Snapshots | 168
Simulation Period | 168 hours
STORAGE CAPACITY (First-Stage)
Scenario: cold | 0.95 MWh (27.2 m³)
Investment Cost | 47,546 EUR
Annualized Cost | 3,093 EUR/a
Scenario: medium | 0.95 MWh (27.2 m³)
Investment Cost | 47,546 EUR
Annualized Cost | 3,093 EUR/a
Scenario: warm | 0.95 MWh (27.2 m³)
Investment Cost | 47,546 EUR
Annualized Cost | 3,093 EUR/a
SCENARIO WEIGHTS
cold | 25.00%
medium | 50.00%
warm | 25.00%

## Buses
scenario | name | v_nom | type | x | y | carrier | unit | location | v_mag_pu_set | v_mag_pu_min | v_mag_pu_max | control | generator | sub_network
cold | bus_heat | 1 |  | 0 | 0 | heat |  |  | 1 | 0 | inf | PQ |  | 0
| bus_electricity | 1 |  | 1 | 0 | electricity |  |  | 1 | 0 | inf | PQ |  | 1
medium | bus_heat | 1 |  | 0 | 0 | heat |  |  | 1 | 0 | inf | PQ |  | 0
| bus_electricity | 1 |  | 1 | 0 | electricity |  |  | 1 | 0 | inf | PQ |  | 1
warm | bus_heat | 1 |  | 0 | 0 | heat |  |  | 1 | 0 | inf | PQ |  | 0
| bus_electricity | 1 |  | 1 | 0 | electricity |  |  | 1 | 0 | inf | PQ |  | 1

## Carriers
scenario | name | co2_emissions | color | nice_name | max_growth | max_relative_growth
cold | heat | 0 | #d62728 |  | inf | 0
| electricity | 0.3 | #1f77b4 |  | inf | 0
medium | heat | 0 | #d62728 |  | inf | 0
| electricity | 0.3 | #1f77b4 |  | inf | 0
warm | heat | 0 | #d62728 |  | inf | 0
| electricity | 0.3 | #1f77b4 |  | inf | 0

## Generators
scenario | name | bus | control | type | p_nom | p_nom_mod | p_nom_extendable | p_nom_min | p_nom_max | p_nom_set | p_min_pu | p_max_pu | p_set | e_sum_min | e_sum_max | q_set | sign | carrier | marginal_cost | marginal_cost_quadratic | active | build_year | lifetime | capital_cost | efficiency | committable | start_up_cost | shut_down_cost | stand_by_cost | min_up_time | min_down_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | weight | p_nom_opt
cold | grid_electricity | bus_electricity | PQ |  | 10 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | electricity | 80 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 10
| peak_boiler | bus_heat | PQ |  | 5 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | heat | 120 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 5
medium | grid_electricity | bus_electricity | PQ |  | 10 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | electricity | 80 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 10
| peak_boiler | bus_heat | PQ |  | 5 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | heat | 120 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 5
warm | grid_electricity | bus_electricity | PQ |  | 10 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | electricity | 80 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 10
| peak_boiler | bus_heat | PQ |  | 5 | 0 | FALSE | 0 | inf |  | 0 | 1 |  | -inf | inf | 0 | 1 | heat | 120 | 0 | TRUE | 0 | inf | 0 | 1 | FALSE | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 5

## Links
scenario | name | bus0 | bus1 | type | carrier | efficiency | active | build_year | lifetime | p_nom | p_nom_mod | p_nom_extendable | p_nom_min | p_nom_max | p_nom_set | p_set | p_min_pu | p_max_pu | capital_cost | marginal_cost | marginal_cost_quadratic | stand_by_cost | length | terrain_factor | committable | start_up_cost | shut_down_cost | min_up_time | min_down_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | p_nom_opt
cold | heat_pump | bus_electricity | bus_heat |  | heat | 1 | TRUE | 0 | inf | 0.6 | 0 | FALSE | 0 | inf |  |  | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | TRUE | 50 | 0 | 2 | 1 | 1 | 0 |  |  | 1 | 1 | 0.6
medium | heat_pump | bus_electricity | bus_heat |  | heat | 1 | TRUE | 0 | inf | 0.6 | 0 | FALSE | 0 | inf |  |  | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | TRUE | 50 | 0 | 2 | 1 | 1 | 0 |  |  | 1 | 1 | 0.6
warm | heat_pump | bus_electricity | bus_heat |  | heat | 1 | TRUE | 0 | inf | 0.6 | 0 | FALSE | 0 | inf |  |  | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | TRUE | 50 | 0 | 2 | 1 | 1 | 0 |  |  | 1 | 1 | 0.6

## Stores
scenario | name | bus | type | carrier | e_nom | e_nom_mod | e_nom_extendable | e_nom_min | e_nom_max | e_nom_set | e_min_pu | e_max_pu | e_initial | e_initial_per_period | e_cyclic | e_cyclic_per_period | p_set | q_set | e_set | sign | marginal_cost | marginal_cost_quadratic | marginal_cost_storage | capital_cost | standing_loss | active | build_year | lifetime | e_nom_opt
cold | thermal_storage | bus_heat |  | heat | 0 | 0 | TRUE | 0.1 | 20 |  | 0 | 1 | 0.5 | FALSE | FALSE | FALSE |  | 0 |  | 1 | 0 | 0 | 0 | 3238.4385 | 0.02 | TRUE | 0 | inf | 0.94946
medium | thermal_storage | bus_heat |  | heat | 0 | 0 | TRUE | 0.1 | 20 |  | 0 | 1 | 0.5 | FALSE | FALSE | FALSE |  | 0 |  | 1 | 0 | 0 | 0 | 3238.4385 | 0.02 | TRUE | 0 | inf | 0.94946
warm | thermal_storage | bus_heat |  | heat | 0 | 0 | TRUE | 0.1 | 20 |  | 0 | 1 | 0.5 | FALSE | FALSE | FALSE |  | 0 |  | 1 | 0 | 0 | 0 | 3238.4385 | 0.02 | TRUE | 0 | inf | 0.94946

## Loads
scenario | name | bus | carrier | type | p_set | q_set | sign | active
cold | heat_demand | bus_heat | heat |  | 0 | 0 | -1 | TRUE
medium | heat_demand | bus_heat | heat |  | 0 | 0 | -1 | TRUE
warm | heat_demand | bus_heat | heat |  | 0 | 0 | -1 | TRUE

## Gen_Dispatch
scenario | cold |  | medium |  | warm
name | grid_electricity | peak_boiler | grid_electricity | peak_boiler | grid_electricity | peak_boiler
snapshot
2024-01-01 | 0.27507 | 0 | 0.18159 | 0 | 0.18 | 0
2024-01-01 01:00 | -1.9813e-17 | 0 | 1.9813e-17 | 0 | 0 | 0
2024-01-01 02:00 | -2.972e-17 | 0 | -1.9813e-17 | 0 | -4.3342e-18 | 0
2024-01-01 03:00 | -1.9814e-17 | 0.12879 | 0.18 | 0 | 0.18 | 0
2024-01-01 04:00 | 0 | 0.39545 | 0.18 | 0 | 0.18 | 0
2024-01-01 05:00 | 0 | 0.42194 | 0.18 | 0 | 0.18 | 0
2024-01-01 06:00 | -1.9814e-17 | 0.44472 | 0.18 | 0 | 0.21058 | 0
2024-01-01 07:00 | 0 | 0.46124 | 0.18 | 0 | 0.18 | 0
2024-01-01 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 11:00 | 0.18 | 0 | 1.9813e-17 | 0 | 0.18 | 0
2024-01-01 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 13:00 | 0.18 | 0 | 0.18 | 0 | -3.9627e-17 | 0
2024-01-01 14:00 | 0.42374 | 0 | 0.18 | 0 | -3.4673e-17 | 0
2024-01-01 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 17:00 | 1.9813e-17 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 18:00 | 2.4767e-18 | 0.003535 | 0.18 | 0 | 0.18 | 0
2024-01-01 19:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 20:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 21:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-01 22:00 | 0.18 | 0 | 3.9627e-17 | 0 | 0.18 | 0
2024-01-01 23:00 | 0.18 | 0 | -1.486e-17 | 0 | 0.18 | 0
2024-01-02 | 0.18 | 0 | 0.18 | 0 | -1.9813e-17 | 0
2024-01-02 01:00 | 0.18 | 0 | 0.18 | 0 | 7.9253e-17 | 0
2024-01-02 02:00 | 0.18 | 0 | 0.18 | 0 | 9.9067e-18 | 0.13687
2024-01-02 03:00 | 0.18 | 0 | 0.18 | 0 | 5.944e-17 | 0.38023
2024-01-02 04:00 | 0.18 | 0 | 9.9067e-18 | 0 | 0.35967 | 0
2024-01-02 05:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 06:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 07:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 13:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 14:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 17:00 | 0.18 | 0 | 0.18 | 0 | 3.9627e-17 | 0
2024-01-02 18:00 | 0.18 | 0 | 0.18 | 0 | 1.9813e-17 | 0
2024-01-02 19:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 20:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 21:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 22:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-02 23:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 01:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 02:00 | 0.18 | 0 | 0.18 | 0 | 0.25725 | 0
2024-01-03 03:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 04:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 05:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 06:00 | 0.18 | 0 | 0.18 | 0 | -1.9813e-17 | 0
2024-01-03 07:00 | 0.18 | 0 | 0.18 | 0 | 1.486e-17 | 0.053809
2024-01-03 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 13:00 | 0.18 | 0 | 0.18695 | 0 | 0.18 | 0
2024-01-03 14:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 17:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 18:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 19:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 20:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 21:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-03 22:00 | 0.18 | 0 | -3.9627e-17 | 0 | 0.18 | 0
2024-01-03 23:00 | 0.18 | 0 | 2.4767e-17 | 0 | 0.18 | 0
2024-01-04 | 0.18 | 0 | -3.9627e-17 | 0.25124 | -9.9067e-17 | 0
2024-01-04 01:00 | 0.18 | 0 | 0.18 | 0 | 1.9813e-17 | 0
2024-01-04 02:00 | 0.18 | 0 | 0.18 | 0 | -9.9067e-18 | 0.14411
2024-01-04 03:00 | 0.34996 | 0 | 0.18 | 0 | -1.9813e-17 | 0.39176
2024-01-04 04:00 | 0.19048 | 0 | 0.18 | 0 | 0 | 0.42082
2024-01-04 05:00 | 0.19994 | 0 | 0.18 | 0 | 0.3539 | 0
2024-01-04 06:00 | 0.20776 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 07:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 13:00 | 0.18 | 0 | 0.21755 | 0 | 0.18 | 0
2024-01-04 14:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 17:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 18:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 19:00 | 0.18367 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 20:00 | 0.19077 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 21:00 | 0.18506 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-04 22:00 | 0.18 | 0 | -3.9627e-17 | 0 | 0.18 | 0
2024-01-04 23:00 | 0.18 | 0 | -9.9067e-18 | 0 | 0.18 | 0
2024-01-05 | 0.18 | 0 | -4.458e-17 | 0.26493 | 0.18 | 0
2024-01-05 01:00 | 0.18 | 0 | 0.18 | 0 | 0.18639 | 0
2024-01-05 02:00 | 0.18 | 0 | 0.18 | 0 | 0.19388 | 0
2024-01-05 03:00 | 0.18 | 0 | 0.18 | 0 | 0.2031 | 0
2024-01-05 04:00 | 0.5047 | 0 | 0.18 | 0 | 0.55169 | 0
2024-01-05 05:00 | 0.20864 | 0 | 0.18 | 0 | 0.22827 | 0
2024-01-05 06:00 | 0.21572 | 0 | 0.18 | 0 | 0.22743 | 0
2024-01-05 07:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 13:00 | 0.18 | 0 | 0.18 | 0 | 0.5035 | 0
2024-01-05 14:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 16:00 | 0.18806 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 17:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 18:00 | 0.19844 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 19:00 | 0.19513 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-05 20:00 | 0.19018 | 0 | 0.18 | 0 | 0.21272 | 0
2024-01-05 21:00 | 0.18351 | 0 | 0.18 | 0 | 0.20644 | 0
2024-01-05 22:00 | 0.18 | 0 | 0.18 | 0 | 0.19952 | 0
2024-01-05 23:00 | 0.18 | 0 | 0.18 | 0 | 0.19329 | 0
2024-01-06 | 0.18 | 0 | 0.18 | 0 | 0.18849 | 0
2024-01-06 01:00 | 0.18 | 0 | 0.18 | 0 | 0.19087 | 0
2024-01-06 02:00 | 0.18 | 0 | 0.18 | 0 | 0.19536 | 0
2024-01-06 03:00 | 0.20258 | 0 | 0.18 | 0 | 0.20168 | 0
2024-01-06 04:00 | 0.18 | 0 | 0.18 | 0 | 0.24549 | 0
2024-01-06 05:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 06:00 | 0.18 | 0 | 0.18 | 0 | 0.56062 | 0
2024-01-06 07:00 | 0.55244 | 0 | 0.18 | 0 | 0.1967 | 0
2024-01-06 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 13:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 14:00 | 0.18 | 0 | 0.18 | 0 | 0.38572 | 0
2024-01-06 15:00 | 0.20897 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 17:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 18:00 | 0.20873 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-06 19:00 | 0.22758 | 0 | 0.18 | 0 | 0.21231 | 0
2024-01-06 20:00 | 0.18 | 0 | 0.18 | 0 | 0.20757 | 0
2024-01-06 21:00 | 0.19522 | 0 | 0.18 | 0 | 0.20148 | 0
2024-01-06 22:00 | 0.1886 | 0 | 0.18 | 0 | 0.19494 | 0
2024-01-06 23:00 | 0.18271 | 0 | 0.18 | 0 | 0.19273 | 0
2024-01-07 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 01:00 | 0.18 | 0 | 0.18 | 0 | 0.18633 | 0
2024-01-07 02:00 | 0.18748 | 0 | 0.18 | 0 | 0.19136 | 0
2024-01-07 03:00 | 0.19618 | 0 | 0.18 | 0 | 0.19839 | 0
2024-01-07 04:00 | 0.54441 | 0 | 0.18 | 0 | 0.2065 | 0
2024-01-07 05:00 | 0.2212 | 0 | 0.18 | 0 | 0.55341 | 0
2024-01-07 06:00 | 0.22827 | 0 | 0.18 | 0 | 0.22069 | 0
2024-01-07 07:00 | 0.23272 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 08:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 09:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 10:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 11:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 12:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 13:00 | 0.18 | 0 | 0.18 | 0 | 0.23141 | 0
2024-01-07 14:00 | 0.29684 | 0 | 0.18 | 0 | 0.53162 | 0
2024-01-07 15:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 16:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 17:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 18:00 | 0.18 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 19:00 | 0.20554 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 20:00 | 0.20053 | 0 | 0.18 | 0 | 0.18 | 0
2024-01-07 21:00 | 0.19392 | 0 | 0.18 | 0 | 0.21694 | 0
2024-01-07 22:00 | 0.18671 | 0 | 0.18 | 0 | 0.21182 | 0
2024-01-07 23:00 | 0.18039 | 0 | -1.9813e-17 | 0 | 0.20723 | 0

## Gen_MarginalCost
scenario | cold | medium | warm
name | grid_electricity | grid_electricity | grid_electricity
snapshot
2024-01-01 | 50.87 | 68.7991 | 0.1
2024-01-01 01:00 | 48.19 | 62.6844 | 0.01
2024-01-01 02:00 | 44.68 | 60.2004 | 0
2024-01-01 03:00 | 42.92 | 56.3537 | -0.01
2024-01-01 04:00 | 40.39 | 55.4695 | -0.03
2024-01-01 05:00 | 40.2 | 54.9571 | -0.02
2024-01-01 06:00 | 39.63 | 53.5324 | -0.05
2024-01-01 07:00 | 40.09 | 60.9146 | -0.02
2024-01-01 08:00 | 41.27 | 64.9195 | 0
2024-01-01 09:00 | 44.88 | 64.6992 | 0.04
2024-01-01 10:00 | 45 | 60.8954 | 0.06
2024-01-01 11:00 | 47.2 | 60.344 | 0.54
2024-01-01 12:00 | 50.78 | 57.8528 | 2.24
2024-01-01 13:00 | 45.49 | 55.4409 | 1.96
2024-01-01 14:00 | 44.73 | 59.8816 | 1.04
2024-01-01 15:00 | 46.59 | 66.6941 | 3.66
2024-01-01 16:00 | 52.99 | 76.5461 | 43.06
2024-01-01 17:00 | 60.26 | 88.4034 | 49.93
2024-01-01 18:00 | 60.61 | 91.3571 | 58
2024-01-01 19:00 | 60.36 | 87.1599 | 54.25
2024-01-01 20:00 | 57.4 | 79.5799 | 48.01
2024-01-01 21:00 | 53.86 | 73.3514 | 42.95
2024-01-01 22:00 | 53.45 | 71.4214 | 47.09
2024-01-01 23:00 | 49.72 | 63.5831 | 35.55
2024-01-02 | 46.69 | 78.564 | 30.59
2024-01-02 01:00 | 42.43 | 73.7752 | 20.07
2024-01-02 02:00 | 41.09 | 71.1156 | 31.03
2024-01-02 03:00 | 40 | 68.0837 | 18.39
2024-01-02 04:00 | 37.55 | 67.7188 | 11.08
2024-01-02 05:00 | 39 | 69.6363 | 13.78
2024-01-02 06:00 | 42.09 | 77.3715 | 47.63
2024-01-02 07:00 | 44.96 | 92.7204 | 58.1
2024-01-02 08:00 | 48.45 | 106.1665 | 65.67
2024-01-02 09:00 | 52 | 97.493 | 64.73
2024-01-02 10:00 | 52 | 86.3332 | 68.98
2024-01-02 11:00 | 52.15 | 79.8596 | 73.54
2024-01-02 12:00 | 55.95 | 74.8658 | 78.16
2024-01-02 13:00 | 52 | 73.5743 | 78.87
2024-01-02 14:00 | 50.69 | 79.5221 | 79.24
2024-01-02 15:00 | 53.45 | 90.9303 | 79.96
2024-01-02 16:00 | 59.99 | 104.1423 | 83.46
2024-01-02 17:00 | 62 | 117.4899 | 80.92
2024-01-02 18:00 | 63.08 | 121.3437 | 74.95
2024-01-02 19:00 | 62.17 | 115.3367 | 63.18
2024-01-02 20:00 | 60.03 | 99.2993 | 57.11
2024-01-02 21:00 | 55.03 | 91.2112 | 46.89
2024-01-02 22:00 | 52.25 | 86.67 | 40
2024-01-02 23:00 | 48.45 | 77.5908 | 7.43
2024-01-03 | 46.11 | 75.0452 | -0.08
2024-01-03 01:00 | 43 | 70.2589 | -1.23
2024-01-03 02:00 | 39.55 | 68.2031 | -1.3
2024-01-03 03:00 | 35.18 | 64.9565 | -1.31
2024-01-03 04:00 | 33.45 | 63.9718 | -1.31
2024-01-03 05:00 | 32.37 | 64.2554 | -1.38
2024-01-03 06:00 | 31.7 | 66.2302 | 1.09
2024-01-03 07:00 | 32.63 | 77.5676 | 40.59
2024-01-03 08:00 | 36.9 | 85.7614 | 59.61
2024-01-03 09:00 | 36.96 | 84.0552 | 60.61
2024-01-03 10:00 | 36.96 | 79.2401 | 57
2024-01-03 11:00 | 43.72 | 76.7767 | 54.89
2024-01-03 12:00 | 47.71 | 73.843 | 53.89
2024-01-03 13:00 | 40.41 | 71.9152 | 54.42
2024-01-03 14:00 | 39.66 | 75.5381 | 60.86
2024-01-03 15:00 | 39.57 | 83.0527 | 67.18
2024-01-03 16:00 | 36.11 | 92.873 | 73.59
2024-01-03 17:00 | 45.04 | 103.7354 | 82.28
2024-01-03 18:00 | 52.56 | 107.241 | 82.97
2024-01-03 19:00 | 45.84 | 102.2051 | 79.03
2024-01-03 20:00 | 35.83 | 92.5188 | 73.23
2024-01-03 21:00 | 33.31 | 84.9725 | 67.41
2024-01-03 22:00 | 34.98 | 80.9922 | 65
2024-01-03 23:00 | 27.39 | 72.0982 | 58.12
2024-01-04 | 29.33 | 70.6332 | 57.3
2024-01-04 01:00 | 24.82 | 64.5142 | 50.46
2024-01-04 02:00 | 24.65 | 62.0232 | 40
2024-01-04 03:00 | 24.8 | 58.172 | 25.48
2024-01-04 04:00 | 27.71 | 57.3079 | 35
2024-01-04 05:00 | 28.58 | 56.7028 | 57.73
2024-01-04 06:00 | 37.04 | 54.3837 | 72.65
2024-01-04 07:00 | 52.03 | 61.7787 | 85.02
2024-01-04 08:00 | 55.76 | 65.8534 | 91.47
2024-01-04 09:00 | 57.06 | 65.6572 | 94.2
2024-01-04 10:00 | 57.18 | 61.8246 | 91.61
2024-01-04 11:00 | 60 | 61.2801 | 90.03
2024-01-04 12:00 | 61.27 | 58.6641 | 86.3
2024-01-04 13:00 | 60.28 | 56.2052 | 85.96
2024-01-04 14:00 | 60.07 | 60.6597 | 92.11
2024-01-04 15:00 | 59.46 | 67.3378 | 98.62
2024-01-04 16:00 | 61.99 | 77.3115 | 105.73
2024-01-04 17:00 | 66.82 | 89.3361 | 133.23
2024-01-04 18:00 | 61.97 | 92.4683 | 144.65
2024-01-04 19:00 | 55.06 | 88.1474 | 125
2024-01-04 20:00 | 47.34 | 80.4239 | 103.59
2024-01-04 21:00 | 45.64 | 74.127 | 100.01
2024-01-04 22:00 | 48.93 | 72.0598 | 94.86
2024-01-04 23:00 | 44.64 | 64.1771 | 88.83
2024-01-05 | 37.54 | 73.2737 | 86.08
2024-01-05 01:00 | 40.07 | 69.818 | 80.51
2024-01-05 02:00 | 39.81 | 67.4332 | 77.01
2024-01-05 03:00 | 39.65 | 63.4706 | 73.21
2024-01-05 04:00 | 40.2 | 64.8361 | 74.05
2024-01-05 05:00 | 44.26 | 74.6507 | 76.03
2024-01-05 06:00 | 47.06 | 101.6298 | 81
2024-01-05 07:00 | 54.96 | 131.6329 | 87
2024-01-05 08:00 | 63.67 | 157.009 | 89.57
2024-01-05 09:00 | 64.73 | 130.249 | 94.93
2024-01-05 10:00 | 66.07 | 105.2677 | 96.28
2024-01-05 11:00 | 65.97 | 91.1246 | 98.22
2024-01-05 12:00 | 65.46 | 83.4055 | 92.24
2024-01-05 13:00 | 63.82 | 85.8592 | 91.54
2024-01-05 14:00 | 63.87 | 97.6 | 96.41
2024-01-05 15:00 | 64.05 | 119.1315 | 100.05
2024-01-05 16:00 | 64.26 | 144.624 | 102.97
2024-01-05 17:00 | 67.14 | 171.4683 | 107.38
2024-01-05 18:00 | 61.61 | 170.022 | 108.45
2024-01-05 19:00 | 59.16 | 154.8672 | 103.96
2024-01-05 20:00 | 59.26 | 111.3572 | 100.09
2024-01-05 21:00 | 53.62 | 98.6806 | 94.19
2024-01-05 22:00 | 53.86 | 90.9188 | 94.92
2024-01-05 23:00 | 47.99 | 81.2917 | 86.8
2024-01-06 | 44.41 | 84.6965 | 82.25
2024-01-06 01:00 | 42.94 | 80.405 | 80.2
2024-01-06 02:00 | 42.88 | 77.1304 | 76.13
2024-01-06 03:00 | 42.15 | 74.5295 | 73.01
2024-01-06 04:00 | 43.23 | 75.2005 | 73.01
2024-01-06 05:00 | 44.56 | 80.2448 | 74.59
2024-01-06 06:00 | 47.4 | 100.4182 | 75.1
2024-01-06 07:00 | 44.05 | 131.5403 | 81.39
2024-01-06 08:00 | 53.41 | 156.7423 | 88.4
2024-01-06 09:00 | 54.8 | 129.8734 | 92.23
2024-01-06 10:00 | 53.94 | 104.5617 | 97.3
2024-01-06 11:00 | 58.3 | 90.3119 | 100.43
2024-01-06 12:00 | 61.43 | 82.5008 | 99.16
2024-01-06 13:00 | 61.92 | 84.9825 | 95.22
2024-01-06 14:00 | 57 | 96.7378 | 92.55
2024-01-06 15:00 | 57.53 | 118.5294 | 95.09
2024-01-06 16:00 | 61.68 | 144.3045 | 99.85
2024-01-06 17:00 | 61.84 | 171.4315 | 104.27
2024-01-06 18:00 | 57.46 | 170.0681 | 103.63
2024-01-06 19:00 | 58.06 | 154.9092 | 99
2024-01-06 20:00 | 59.97 | 121.352 | 92.14
2024-01-06 21:00 | 52.95 | 107.537 | 88
2024-01-06 22:00 | 52.95 | 99.0782 | 86.57
2024-01-06 23:00 | 49.53 | 88.5867 | 79.87
2024-01-07 | 51.03 | 85.1118 | 84.08
2024-01-07 01:00 | 50.18 | 80.7992 | 79.82
2024-01-07 02:00 | 48.97 | 77.5085 | 76.76
2024-01-07 03:00 | 46.72 | 74.8948 | 73.46
2024-01-07 04:00 | 46.87 | 75.5692 | 71.86
2024-01-07 05:00 | 50.08 | 80.6382 | 72.08
2024-01-07 06:00 | 57.34 | 100.9106 | 74.9
2024-01-07 07:00 | 67.8 | 132.1855 | 77.69
2024-01-07 08:00 | 86.51 | 156.754 | 81.79
2024-01-07 09:00 | 86.54 | 129.8831 | 84.86
2024-01-07 10:00 | 85.08 | 104.5696 | 87.15
2024-01-07 11:00 | 88.74 | 90.3187 | 89.14
2024-01-07 12:00 | 88.76 | 82.507 | 88.66
2024-01-07 13:00 | 84.31 | 84.9889 | 84.81
2024-01-07 14:00 | 80.4 | 96.7451 | 84.34
2024-01-07 15:00 | 83.57 | 118.5383 | 88.01
2024-01-07 16:00 | 89.68 | 144.3153 | 93.42
2024-01-07 17:00 | 100 | 171.4443 | 101.77
2024-01-07 18:00 | 90.43 | 170.0808 | 104.85
2024-01-07 19:00 | 80.28 | 154.9208 | 103.55
2024-01-07 20:00 | 66.8 | 121.9471 | 100.5
2024-01-07 21:00 | 60.22 | 108.0644 | 93.31
2024-01-07 22:00 | 59.69 | 99.564 | 91.17
2024-01-07 23:00 | 52.25 | 89.0211 | 83.86

## Link_P0_Electricity
scenario | cold | medium | warm
name | heat_pump | heat_pump | heat_pump
snapshot
2024-01-01 | 0.27507 | 0.18159 | 0.18
2024-01-01 01:00 | -1.9813e-17 | 1.9813e-17 | 0
2024-01-01 02:00 | -2.972e-17 | -1.9813e-17 | -4.3342e-18
2024-01-01 03:00 | -1.9814e-17 | 0.18 | 0.18
2024-01-01 04:00 | 0 | 0.18 | 0.18
2024-01-01 05:00 | 0 | 0.18 | 0.18
2024-01-01 06:00 | -1.9814e-17 | 0.18 | 0.21058
2024-01-01 07:00 | 0 | 0.18 | 0.18
2024-01-01 08:00 | 0.18 | 0.18 | 0.18
2024-01-01 09:00 | 0.18 | 0.18 | 0.18
2024-01-01 10:00 | 0.18 | 0.18 | 0.18
2024-01-01 11:00 | 0.18 | 1.9813e-17 | 0.18
2024-01-01 12:00 | 0.18 | 0.18 | 0.18
2024-01-01 13:00 | 0.18 | 0.18 | -3.9627e-17
2024-01-01 14:00 | 0.42374 | 0.18 | -3.4673e-17
2024-01-01 15:00 | 0.18 | 0.18 | 0.18
2024-01-01 16:00 | 0.18 | 0.18 | 0.18
2024-01-01 17:00 | 1.9813e-17 | 0.18 | 0.18
2024-01-01 18:00 | 2.4767e-18 | 0.18 | 0.18
2024-01-01 19:00 | 0.18 | 0.18 | 0.18
2024-01-01 20:00 | 0.18 | 0.18 | 0.18
2024-01-01 21:00 | 0.18 | 0.18 | 0.18
2024-01-01 22:00 | 0.18 | 3.9627e-17 | 0.18
2024-01-01 23:00 | 0.18 | -1.486e-17 | 0.18
2024-01-02 | 0.18 | 0.18 | -1.9813e-17
2024-01-02 01:00 | 0.18 | 0.18 | 7.9253e-17
2024-01-02 02:00 | 0.18 | 0.18 | 9.9067e-18
2024-01-02 03:00 | 0.18 | 0.18 | 5.944e-17
2024-01-02 04:00 | 0.18 | 9.9067e-18 | 0.35967
2024-01-02 05:00 | 0.18 | 0.18 | 0.18
2024-01-02 06:00 | 0.18 | 0.18 | 0.18
2024-01-02 07:00 | 0.18 | 0.18 | 0.18
2024-01-02 08:00 | 0.18 | 0.18 | 0.18
2024-01-02 09:00 | 0.18 | 0.18 | 0.18
2024-01-02 10:00 | 0.18 | 0.18 | 0.18
2024-01-02 11:00 | 0.18 | 0.18 | 0.18
2024-01-02 12:00 | 0.18 | 0.18 | 0.18
2024-01-02 13:00 | 0.18 | 0.18 | 0.18
2024-01-02 14:00 | 0.18 | 0.18 | 0.18
2024-01-02 15:00 | 0.18 | 0.18 | 0.18
2024-01-02 16:00 | 0.18 | 0.18 | 0.18
2024-01-02 17:00 | 0.18 | 0.18 | 3.9627e-17
2024-01-02 18:00 | 0.18 | 0.18 | 1.9813e-17
2024-01-02 19:00 | 0.18 | 0.18 | 0.18
2024-01-02 20:00 | 0.18 | 0.18 | 0.18
2024-01-02 21:00 | 0.18 | 0.18 | 0.18
2024-01-02 22:00 | 0.18 | 0.18 | 0.18
2024-01-02 23:00 | 0.18 | 0.18 | 0.18
2024-01-03 | 0.18 | 0.18 | 0.18
2024-01-03 01:00 | 0.18 | 0.18 | 0.18
2024-01-03 02:00 | 0.18 | 0.18 | 0.25725
2024-01-03 03:00 | 0.18 | 0.18 | 0.18
2024-01-03 04:00 | 0.18 | 0.18 | 0.18
2024-01-03 05:00 | 0.18 | 0.18 | 0.18
2024-01-03 06:00 | 0.18 | 0.18 | -1.9813e-17
2024-01-03 07:00 | 0.18 | 0.18 | 1.486e-17
2024-01-03 08:00 | 0.18 | 0.18 | 0.18
2024-01-03 09:00 | 0.18 | 0.18 | 0.18
2024-01-03 10:00 | 0.18 | 0.18 | 0.18
2024-01-03 11:00 | 0.18 | 0.18 | 0.18
2024-01-03 12:00 | 0.18 | 0.18 | 0.18
2024-01-03 13:00 | 0.18 | 0.18695 | 0.18
2024-01-03 14:00 | 0.18 | 0.18 | 0.18
2024-01-03 15:00 | 0.18 | 0.18 | 0.18
2024-01-03 16:00 | 0.18 | 0.18 | 0.18
2024-01-03 17:00 | 0.18 | 0.18 | 0.18
2024-01-03 18:00 | 0.18 | 0.18 | 0.18
2024-01-03 19:00 | 0.18 | 0.18 | 0.18
2024-01-03 20:00 | 0.18 | 0.18 | 0.18
2024-01-03 21:00 | 0.18 | 0.18 | 0.18
2024-01-03 22:00 | 0.18 | -3.9627e-17 | 0.18
2024-01-03 23:00 | 0.18 | 2.4767e-17 | 0.18
2024-01-04 | 0.18 | -3.9627e-17 | -9.9067e-17
2024-01-04 01:00 | 0.18 | 0.18 | 1.9813e-17
2024-01-04 02:00 | 0.18 | 0.18 | -9.9067e-18
2024-01-04 03:00 | 0.34996 | 0.18 | -1.9813e-17
2024-01-04 04:00 | 0.19048 | 0.18 | 0
2024-01-04 05:00 | 0.19994 | 0.18 | 0.3539
2024-01-04 06:00 | 0.20776 | 0.18 | 0.18
2024-01-04 07:00 | 0.18 | 0.18 | 0.18
2024-01-04 08:00 | 0.18 | 0.18 | 0.18
2024-01-04 09:00 | 0.18 | 0.18 | 0.18
2024-01-04 10:00 | 0.18 | 0.18 | 0.18
2024-01-04 11:00 | 0.18 | 0.18 | 0.18
2024-01-04 12:00 | 0.18 | 0.18 | 0.18
2024-01-04 13:00 | 0.18 | 0.21755 | 0.18
2024-01-04 14:00 | 0.18 | 0.18 | 0.18
2024-01-04 15:00 | 0.18 | 0.18 | 0.18
2024-01-04 16:00 | 0.18 | 0.18 | 0.18
2024-01-04 17:00 | 0.18 | 0.18 | 0.18
2024-01-04 18:00 | 0.18 | 0.18 | 0.18
2024-01-04 19:00 | 0.18367 | 0.18 | 0.18
2024-01-04 20:00 | 0.19077 | 0.18 | 0.18
2024-01-04 21:00 | 0.18506 | 0.18 | 0.18
2024-01-04 22:00 | 0.18 | -3.9627e-17 | 0.18
2024-01-04 23:00 | 0.18 | -9.9067e-18 | 0.18
2024-01-05 | 0.18 | -4.458e-17 | 0.18
2024-01-05 01:00 | 0.18 | 0.18 | 0.18639
2024-01-05 02:00 | 0.18 | 0.18 | 0.19388
2024-01-05 03:00 | 0.18 | 0.18 | 0.2031
2024-01-05 04:00 | 0.5047 | 0.18 | 0.55169
2024-01-05 05:00 | 0.20864 | 0.18 | 0.22827
2024-01-05 06:00 | 0.21572 | 0.18 | 0.22743
2024-01-05 07:00 | 0.18 | 0.18 | 0.18
2024-01-05 08:00 | 0.18 | 0.18 | 0.18
2024-01-05 09:00 | 0.18 | 0.18 | 0.18
2024-01-05 10:00 | 0.18 | 0.18 | 0.18
2024-01-05 11:00 | 0.18 | 0.18 | 0.18
2024-01-05 12:00 | 0.18 | 0.18 | 0.18
2024-01-05 13:00 | 0.18 | 0.18 | 0.5035
2024-01-05 14:00 | 0.18 | 0.18 | 0.18
2024-01-05 15:00 | 0.18 | 0.18 | 0.18
2024-01-05 16:00 | 0.18806 | 0.18 | 0.18
2024-01-05 17:00 | 0.18 | 0.18 | 0.18
2024-01-05 18:00 | 0.19844 | 0.18 | 0.18
2024-01-05 19:00 | 0.19513 | 0.18 | 0.18
2024-01-05 20:00 | 0.19018 | 0.18 | 0.21272
2024-01-05 21:00 | 0.18351 | 0.18 | 0.20644
2024-01-05 22:00 | 0.18 | 0.18 | 0.19952
2024-01-05 23:00 | 0.18 | 0.18 | 0.19329
2024-01-06 | 0.18 | 0.18 | 0.18849
2024-01-06 01:00 | 0.18 | 0.18 | 0.19087
2024-01-06 02:00 | 0.18 | 0.18 | 0.19536
2024-01-06 03:00 | 0.20258 | 0.18 | 0.20168
2024-01-06 04:00 | 0.18 | 0.18 | 0.24549
2024-01-06 05:00 | 0.18 | 0.18 | 0.18
2024-01-06 06:00 | 0.18 | 0.18 | 0.56062
2024-01-06 07:00 | 0.55244 | 0.18 | 0.1967
2024-01-06 08:00 | 0.18 | 0.18 | 0.18
2024-01-06 09:00 | 0.18 | 0.18 | 0.18
2024-01-06 10:00 | 0.18 | 0.18 | 0.18
2024-01-06 11:00 | 0.18 | 0.18 | 0.18
2024-01-06 12:00 | 0.18 | 0.18 | 0.18
2024-01-06 13:00 | 0.18 | 0.18 | 0.18
2024-01-06 14:00 | 0.18 | 0.18 | 0.38572
2024-01-06 15:00 | 0.20897 | 0.18 | 0.18
2024-01-06 16:00 | 0.18 | 0.18 | 0.18
2024-01-06 17:00 | 0.18 | 0.18 | 0.18
2024-01-06 18:00 | 0.20873 | 0.18 | 0.18
2024-01-06 19:00 | 0.22758 | 0.18 | 0.21231
2024-01-06 20:00 | 0.18 | 0.18 | 0.20757
2024-01-06 21:00 | 0.19522 | 0.18 | 0.20148
2024-01-06 22:00 | 0.1886 | 0.18 | 0.19494
2024-01-06 23:00 | 0.18271 | 0.18 | 0.19273
2024-01-07 | 0.18 | 0.18 | 0.18
2024-01-07 01:00 | 0.18 | 0.18 | 0.18633
2024-01-07 02:00 | 0.18748 | 0.18 | 0.19136
2024-01-07 03:00 | 0.19618 | 0.18 | 0.19839
2024-01-07 04:00 | 0.54441 | 0.18 | 0.2065
2024-01-07 05:00 | 0.2212 | 0.18 | 0.55341
2024-01-07 06:00 | 0.22827 | 0.18 | 0.22069
2024-01-07 07:00 | 0.23272 | 0.18 | 0.18
2024-01-07 08:00 | 0.18 | 0.18 | 0.18
2024-01-07 09:00 | 0.18 | 0.18 | 0.18
2024-01-07 10:00 | 0.18 | 0.18 | 0.18
2024-01-07 11:00 | 0.18 | 0.18 | 0.18
2024-01-07 12:00 | 0.18 | 0.18 | 0.18
2024-01-07 13:00 | 0.18 | 0.18 | 0.23141
2024-01-07 14:00 | 0.29684 | 0.18 | 0.53162
2024-01-07 15:00 | 0.18 | 0.18 | 0.18
2024-01-07 16:00 | 0.18 | 0.18 | 0.18
2024-01-07 17:00 | 0.18 | 0.18 | 0.18
2024-01-07 18:00 | 0.18 | 0.18 | 0.18
2024-01-07 19:00 | 0.20554 | 0.18 | 0.18
2024-01-07 20:00 | 0.20053 | 0.18 | 0.18
2024-01-07 21:00 | 0.19392 | 0.18 | 0.21694
2024-01-07 22:00 | 0.18671 | 0.18 | 0.21182
2024-01-07 23:00 | 0.18039 | -1.9813e-17 | 0.20723

## Link_P1_Heat
scenario | cold | medium | warm
name | heat_pump | heat_pump | heat_pump
snapshot
2024-01-01 | -0.77067 | -0.50877 | -0.50431
2024-01-01 01:00 | 5.5511e-17 | -5.5511e-17 | 0
2024-01-01 02:00 | 8.3267e-17 | 5.5511e-17 | 1.2143e-17
2024-01-01 03:00 | 5.5511e-17 | -0.50431 | -0.50431
2024-01-01 04:00 | 0 | -0.50431 | -0.50431
2024-01-01 05:00 | 0 | -0.50431 | -0.50431
2024-01-01 06:00 | 5.5511e-17 | -0.50431 | -0.58998
2024-01-01 07:00 | 0 | -0.50431 | -0.50431
2024-01-01 08:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 09:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 10:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 11:00 | -0.5043 | -5.5511e-17 | -0.50431
2024-01-01 12:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 13:00 | -0.5043 | -0.50431 | 1.1102e-16
2024-01-01 14:00 | -1.1872 | -0.50431 | 9.7145e-17
2024-01-01 15:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 16:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 17:00 | -5.5511e-17 | -0.50431 | -0.50431
2024-01-01 18:00 | -6.9389e-18 | -0.50431 | -0.50431
2024-01-01 19:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 20:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 21:00 | -0.5043 | -0.50431 | -0.50431
2024-01-01 22:00 | -0.5043 | -1.1102e-16 | -0.50431
2024-01-01 23:00 | -0.5043 | 4.1633e-17 | -0.50431
2024-01-02 | -0.5043 | -0.50431 | 5.5511e-17
2024-01-02 01:00 | -0.5043 | -0.50431 | -2.2204e-16
2024-01-02 02:00 | -0.5043 | -0.50431 | -2.7756e-17
2024-01-02 03:00 | -0.5043 | -0.50431 | -1.6653e-16
2024-01-02 04:00 | -0.5043 | -2.7756e-17 | -1.0077
2024-01-02 05:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 06:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 07:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 08:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 09:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 10:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 11:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 12:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 13:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 14:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 15:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 16:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 17:00 | -0.5043 | -0.50431 | -1.1102e-16
2024-01-02 18:00 | -0.5043 | -0.50431 | -5.5511e-17
2024-01-02 19:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 20:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 21:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 22:00 | -0.5043 | -0.50431 | -0.50431
2024-01-02 23:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 | -0.5043 | -0.50431 | -0.50431
2024-01-03 01:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 02:00 | -0.5043 | -0.50431 | -0.72073
2024-01-03 03:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 04:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 05:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 06:00 | -0.5043 | -0.50431 | 5.5511e-17
2024-01-03 07:00 | -0.5043 | -0.50431 | -4.1633e-17
2024-01-03 08:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 09:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 10:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 11:00 | -0.5043 | -0.50431 | -0.5043
2024-01-03 12:00 | -0.5043 | -0.50431 | -0.5043
2024-01-03 13:00 | -0.5043 | -0.52378 | -0.5043
2024-01-03 14:00 | -0.5043 | -0.50431 | -0.5043
2024-01-03 15:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 16:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 17:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 18:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 19:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 20:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 21:00 | -0.5043 | -0.50431 | -0.50431
2024-01-03 22:00 | -0.5043 | 1.1102e-16 | -0.50431
2024-01-03 23:00 | -0.5043 | -6.9389e-17 | -0.50431
2024-01-04 | -0.5043 | 1.1102e-16 | 2.7756e-16
2024-01-04 01:00 | -0.5043 | -0.50431 | -5.5511e-17
2024-01-04 02:00 | -0.5043 | -0.50431 | 2.7756e-17
2024-01-04 03:00 | -0.98047 | -0.50431 | 5.5511e-17
2024-01-04 04:00 | -0.53368 | -0.50431 | 0
2024-01-04 05:00 | -0.56016 | -0.50431 | -0.9915
2024-01-04 06:00 | -0.58207 | -0.50431 | -0.5043
2024-01-04 07:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 08:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 09:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 10:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 11:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 12:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 13:00 | -0.5043 | -0.60951 | -0.5043
2024-01-04 14:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 15:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 16:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 17:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 18:00 | -0.5043 | -0.50431 | -0.5043
2024-01-04 19:00 | -0.51458 | -0.50431 | -0.5043
2024-01-04 20:00 | -0.53449 | -0.50431 | -0.50429
2024-01-04 21:00 | -0.51846 | -0.50431 | -0.50429
2024-01-04 22:00 | -0.5043 | 1.1102e-16 | -0.50429
2024-01-04 23:00 | -0.5043 | 2.7756e-17 | -0.50429
2024-01-05 | -0.5043 | 1.249e-16 | -0.50429
2024-01-05 01:00 | -0.5043 | -0.50431 | -0.52219
2024-01-05 02:00 | -0.5043 | -0.50431 | -0.54319
2024-01-05 03:00 | -0.5043 | -0.50431 | -0.56901
2024-01-05 04:00 | -1.414 | -0.50431 | -1.5456
2024-01-05 05:00 | -0.58454 | -0.50431 | -0.63954
2024-01-05 06:00 | -0.60437 | -0.5043 | -0.63719
2024-01-05 07:00 | -0.5043 | -0.5043 | -0.5043
2024-01-05 08:00 | -0.5043 | -0.5043 | -0.5043
2024-01-05 09:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 10:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 11:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 12:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 13:00 | -0.5043 | -0.50431 | -1.4106
2024-01-05 14:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 15:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 16:00 | -0.52687 | -0.50431 | -0.5043
2024-01-05 17:00 | -0.5043 | -0.50431 | -0.5043
2024-01-05 18:00 | -0.55596 | -0.50431 | -0.50429
2024-01-05 19:00 | -0.5467 | -0.50431 | -0.50429
2024-01-05 20:00 | -0.53283 | -0.5043 | -0.59596
2024-01-05 21:00 | -0.51414 | -0.5043 | -0.57836
2024-01-05 22:00 | -0.5043 | -0.50431 | -0.55899
2024-01-05 23:00 | -0.5043 | -0.5043 | -0.54152
2024-01-06 | -0.5043 | -0.5043 | -0.52809
2024-01-06 01:00 | -0.5043 | -0.5043 | -0.53475
2024-01-06 02:00 | -0.5043 | -0.5043 | -0.54732
2024-01-06 03:00 | -0.56756 | -0.5043 | -0.56503
2024-01-06 04:00 | -0.5043 | -0.5043 | -0.68777
2024-01-06 05:00 | -0.5043 | -0.5043 | -0.5043
2024-01-06 06:00 | -0.5043 | -0.5043 | -1.5707
2024-01-06 07:00 | -1.5477 | -0.5043 | -0.55108
2024-01-06 08:00 | -0.5043 | -0.5043 | -0.5043
2024-01-06 09:00 | -0.5043 | -0.5043 | -0.5043
2024-01-06 10:00 | -0.5043 | -0.5043 | -0.5043
2024-01-06 11:00 | -0.5043 | -0.50431 | -0.5043
2024-01-06 12:00 | -0.5043 | -0.50431 | -0.5043
2024-01-06 13:00 | -0.5043 | -0.50431 | -0.5043
2024-01-06 14:00 | -0.5043 | -0.50431 | -1.0806
2024-01-06 15:00 | -0.58547 | -0.50431 | -0.5043
2024-01-06 16:00 | -0.5043 | -0.50431 | -0.5043
2024-01-06 17:00 | -0.5043 | -0.50431 | -0.5043
2024-01-06 18:00 | -0.58479 | -0.50431 | -0.50429
2024-01-06 19:00 | -0.63761 | -0.50431 | -0.59481
2024-01-06 20:00 | -0.5043 | -0.50431 | -0.58152
2024-01-06 21:00 | -0.54694 | -0.50431 | -0.56447
2024-01-06 22:00 | -0.52838 | -0.50431 | -0.54615
2024-01-06 23:00 | -0.51189 | -0.5043 | -0.53997
2024-01-07 | -0.5043 | -0.5043 | -0.50429
2024-01-07 01:00 | -0.5043 | -0.5043 | -0.52204
2024-01-07 02:00 | -0.52526 | -0.5043 | -0.53611
2024-01-07 03:00 | -0.54964 | -0.5043 | -0.55582
2024-01-07 04:00 | -1.5253 | -0.5043 | -0.57854
2024-01-07 05:00 | -0.61972 | -0.5043 | -1.5504
2024-01-07 06:00 | -0.63954 | -0.50431 | -0.61828
2024-01-07 07:00 | -0.65201 | -0.50431 | -0.50429
2024-01-07 08:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 09:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 10:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 11:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 12:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 13:00 | -0.5043 | -0.50431 | -0.64831
2024-01-07 14:00 | -0.83166 | -0.50431 | -1.4894
2024-01-07 15:00 | -0.5043 | -0.50431 | -0.50429
2024-01-07 16:00 | -0.5043 | -0.50431 | -0.50428
2024-01-07 17:00 | -0.5043 | -0.50431 | -0.50428
2024-01-07 18:00 | -0.5043 | -0.50431 | -0.50428
2024-01-07 19:00 | -0.57585 | -0.50431 | -0.50428
2024-01-07 20:00 | -0.56181 | -0.50431 | -0.50428
2024-01-07 21:00 | -0.54329 | -0.50431 | -0.60777
2024-01-07 22:00 | -0.5231 | -0.50431 | -0.59343
2024-01-07 23:00 | -0.50538 | 5.5511e-17 | -0.58057

## Link_Efficiency_COP
scenario | cold | medium | warm
name | heat_pump | heat_pump | heat_pump
snapshot
2024-01-01 | 2.8017 | 2.8017 | 2.8017
2024-01-01 01:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 02:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 03:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 04:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 05:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 06:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 07:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 08:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 09:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 10:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 11:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 12:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 13:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 14:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 15:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 16:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 17:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 18:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 19:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 20:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 21:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 22:00 | 2.8017 | 2.8017 | 2.8017
2024-01-01 23:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 | 2.8017 | 2.8017 | 2.8017
2024-01-02 01:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 02:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 03:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 04:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 05:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 06:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 07:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 08:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 09:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 10:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 11:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 12:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 13:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 14:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 15:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 16:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 17:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 18:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 19:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 20:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 21:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 22:00 | 2.8017 | 2.8017 | 2.8017
2024-01-02 23:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 | 2.8017 | 2.8017 | 2.8017
2024-01-03 01:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 02:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 03:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 04:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 05:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 06:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 07:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 08:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 09:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 10:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 11:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 12:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 13:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 14:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 15:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 16:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 17:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 18:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 19:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 20:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 21:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 22:00 | 2.8017 | 2.8017 | 2.8017
2024-01-03 23:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 | 2.8017 | 2.8017 | 2.8017
2024-01-04 01:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 02:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 03:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 04:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 05:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 06:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 07:00 | 2.8017 | 2.8017 | 2.8017
2024-01-04 08:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 09:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 10:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 11:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 12:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 13:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 14:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 15:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 16:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 17:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 18:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 19:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 20:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 21:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 22:00 | 2.8017 | 2.8017 | 2.8016
2024-01-04 23:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 | 2.8017 | 2.8017 | 2.8016
2024-01-05 01:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 02:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 03:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 04:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 05:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 06:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 07:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 08:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 09:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 10:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 11:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 12:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 13:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 14:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 15:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 16:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 17:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 18:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 19:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 20:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 21:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 22:00 | 2.8017 | 2.8017 | 2.8016
2024-01-05 23:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 | 2.8017 | 2.8017 | 2.8016
2024-01-06 01:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 02:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 03:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 04:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 05:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 06:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 07:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 08:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 09:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 10:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 11:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 12:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 13:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 14:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 15:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 16:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 17:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 18:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 19:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 20:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 21:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 22:00 | 2.8017 | 2.8017 | 2.8016
2024-01-06 23:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 | 2.8017 | 2.8017 | 2.8016
2024-01-07 01:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 02:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 03:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 04:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 05:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 06:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 07:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 08:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 09:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 10:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 11:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 12:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 13:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 14:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 15:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 16:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 17:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 18:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 19:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 20:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 21:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 22:00 | 2.8017 | 2.8017 | 2.8016
2024-01-07 23:00 | 2.8017 | 2.8017 | 2.8016

## Link_Status
scenario | cold | medium | warm
name | heat_pump | heat_pump | heat_pump
snapshot
2024-01-01 | 1 | 1 | 1
2024-01-01 01:00 | 0 | 0 | 0
2024-01-01 02:00 | 0 | 0 | 0
2024-01-01 03:00 | 0 | 1 | 1
2024-01-01 04:00 | 0 | 1 | 1
2024-01-01 05:00 | 0 | 1 | 1
2024-01-01 06:00 | 0 | 1 | 1
2024-01-01 07:00 | 0 | 1 | 1
2024-01-01 08:00 | 1 | 1 | 1
2024-01-01 09:00 | 1 | 1 | 1
2024-01-01 10:00 | 1 | 1 | 1
2024-01-01 11:00 | 1 | 0 | 1
2024-01-01 12:00 | 1 | 1 | 1
2024-01-01 13:00 | 1 | 1 | 0
2024-01-01 14:00 | 1 | 1 | 0
2024-01-01 15:00 | 1 | 1 | 1
2024-01-01 16:00 | 1 | 1 | 1
2024-01-01 17:00 | 0 | 1 | 1
2024-01-01 18:00 | 0 | 1 | 1
2024-01-01 19:00 | 1 | 1 | 1
2024-01-01 20:00 | 1 | 1 | 1
2024-01-01 21:00 | 1 | 1 | 1
2024-01-01 22:00 | 1 | 0 | 1
2024-01-01 23:00 | 1 | 0 | 1
2024-01-02 | 1 | 1 | 0
2024-01-02 01:00 | 1 | 1 | 0
2024-01-02 02:00 | 1 | 1 | 0
2024-01-02 03:00 | 1 | 1 | 0
2024-01-02 04:00 | 1 | 0 | 1
2024-01-02 05:00 | 1 | 1 | 1
2024-01-02 06:00 | 1 | 1 | 1
2024-01-02 07:00 | 1 | 1 | 1
2024-01-02 08:00 | 1 | 1 | 1
2024-01-02 09:00 | 1 | 1 | 1
2024-01-02 10:00 | 1 | 1 | 1
2024-01-02 11:00 | 1 | 1 | 1
2024-01-02 12:00 | 1 | 1 | 1
2024-01-02 13:00 | 1 | 1 | 1
2024-01-02 14:00 | 1 | 1 | 1
2024-01-02 15:00 | 1 | 1 | 1
2024-01-02 16:00 | 1 | 1 | 1
2024-01-02 17:00 | 1 | 1 | 0
2024-01-02 18:00 | 1 | 1 | 0
2024-01-02 19:00 | 1 | 1 | 1
2024-01-02 20:00 | 1 | 1 | 1
2024-01-02 21:00 | 1 | 1 | 1
2024-01-02 22:00 | 1 | 1 | 1
2024-01-02 23:00 | 1 | 1 | 1
2024-01-03 | 1 | 1 | 1
2024-01-03 01:00 | 1 | 1 | 1
2024-01-03 02:00 | 1 | 1 | 1
2024-01-03 03:00 | 1 | 1 | 1
2024-01-03 04:00 | 1 | 1 | 1
2024-01-03 05:00 | 1 | 1 | 1
2024-01-03 06:00 | 1 | 1 | 0
2024-01-03 07:00 | 1 | 1 | 0
2024-01-03 08:00 | 1 | 1 | 1
2024-01-03 09:00 | 1 | 1 | 1
2024-01-03 10:00 | 1 | 1 | 1
2024-01-03 11:00 | 1 | 1 | 1
2024-01-03 12:00 | 1 | 1 | 1
2024-01-03 13:00 | 1 | 1 | 1
2024-01-03 14:00 | 1 | 1 | 1
2024-01-03 15:00 | 1 | 1 | 1
2024-01-03 16:00 | 1 | 1 | 1
2024-01-03 17:00 | 1 | 1 | 1
2024-01-03 18:00 | 1 | 1 | 1
2024-01-03 19:00 | 1 | 1 | 1
2024-01-03 20:00 | 1 | 1 | 1
2024-01-03 21:00 | 1 | 1 | 1
2024-01-03 22:00 | 1 | 0 | 1
2024-01-03 23:00 | 1 | 0 | 1
2024-01-04 | 1 | 0 | 0
2024-01-04 01:00 | 1 | 1 | 0
2024-01-04 02:00 | 1 | 1 | 0
2024-01-04 03:00 | 1 | 1 | 0
2024-01-04 04:00 | 1 | 1 | 0
2024-01-04 05:00 | 1 | 1 | 1
2024-01-04 06:00 | 1 | 1 | 1
2024-01-04 07:00 | 1 | 1 | 1
2024-01-04 08:00 | 1 | 1 | 1
2024-01-04 09:00 | 1 | 1 | 1
2024-01-04 10:00 | 1 | 1 | 1
2024-01-04 11:00 | 1 | 1 | 1
2024-01-04 12:00 | 1 | 1 | 1
2024-01-04 13:00 | 1 | 1 | 1
2024-01-04 14:00 | 1 | 1 | 1
2024-01-04 15:00 | 1 | 1 | 1
2024-01-04 16:00 | 1 | 1 | 1
2024-01-04 17:00 | 1 | 1 | 1
2024-01-04 18:00 | 1 | 1 | 1
2024-01-04 19:00 | 1 | 1 | 1
2024-01-04 20:00 | 1 | 1 | 1
2024-01-04 21:00 | 1 | 1 | 1
2024-01-04 22:00 | 1 | 0 | 1
2024-01-04 23:00 | 1 | 0 | 1
2024-01-05 | 1 | 0 | 1
2024-01-05 01:00 | 1 | 1 | 1
2024-01-05 02:00 | 1 | 1 | 1
2024-01-05 03:00 | 1 | 1 | 1
2024-01-05 04:00 | 1 | 1 | 1
2024-01-05 05:00 | 1 | 1 | 1
2024-01-05 06:00 | 1 | 1 | 1
2024-01-05 07:00 | 1 | 1 | 1
2024-01-05 08:00 | 1 | 1 | 1
2024-01-05 09:00 | 1 | 1 | 1
2024-01-05 10:00 | 1 | 1 | 1
2024-01-05 11:00 | 1 | 1 | 1
2024-01-05 12:00 | 1 | 1 | 1
2024-01-05 13:00 | 1 | 1 | 1
2024-01-05 14:00 | 1 | 1 | 1
2024-01-05 15:00 | 1 | 1 | 1
2024-01-05 16:00 | 1 | 1 | 1
2024-01-05 17:00 | 1 | 1 | 1
2024-01-05 18:00 | 1 | 1 | 1
2024-01-05 19:00 | 1 | 1 | 1
2024-01-05 20:00 | 1 | 1 | 1
2024-01-05 21:00 | 1 | 1 | 1
2024-01-05 22:00 | 1 | 1 | 1
2024-01-05 23:00 | 1 | 1 | 1
2024-01-06 | 1 | 1 | 1
2024-01-06 01:00 | 1 | 1 | 1
2024-01-06 02:00 | 1 | 1 | 1
2024-01-06 03:00 | 1 | 1 | 1
2024-01-06 04:00 | 1 | 1 | 1
2024-01-06 05:00 | 1 | 1 | 1
2024-01-06 06:00 | 1 | 1 | 1
2024-01-06 07:00 | 1 | 1 | 1
2024-01-06 08:00 | 1 | 1 | 1
2024-01-06 09:00 | 1 | 1 | 1
2024-01-06 10:00 | 1 | 1 | 1
2024-01-06 11:00 | 1 | 1 | 1
2024-01-06 12:00 | 1 | 1 | 1
2024-01-06 13:00 | 1 | 1 | 1
2024-01-06 14:00 | 1 | 1 | 1
2024-01-06 15:00 | 1 | 1 | 1
2024-01-06 16:00 | 1 | 1 | 1
2024-01-06 17:00 | 1 | 1 | 1
2024-01-06 18:00 | 1 | 1 | 1
2024-01-06 19:00 | 1 | 1 | 1
2024-01-06 20:00 | 1 | 1 | 1
2024-01-06 21:00 | 1 | 1 | 1
2024-01-06 22:00 | 1 | 1 | 1
2024-01-06 23:00 | 1 | 1 | 1
2024-01-07 | 1 | 1 | 1
2024-01-07 01:00 | 1 | 1 | 1
2024-01-07 02:00 | 1 | 1 | 1
2024-01-07 03:00 | 1 | 1 | 1
2024-01-07 04:00 | 1 | 1 | 1
2024-01-07 05:00 | 1 | 1 | 1
2024-01-07 06:00 | 1 | 1 | 1
2024-01-07 07:00 | 1 | 1 | 1
2024-01-07 08:00 | 1 | 1 | 1
2024-01-07 09:00 | 1 | 1 | 1
2024-01-07 10:00 | 1 | 1 | 1
2024-01-07 11:00 | 1 | 1 | 1
2024-01-07 12:00 | 1 | 1 | 1
2024-01-07 13:00 | 1 | 1 | 1
2024-01-07 14:00 | 1 | 1 | 1
2024-01-07 15:00 | 1 | 1 | 1
2024-01-07 16:00 | 1 | 1 | 1
2024-01-07 17:00 | 1 | 1 | 1
2024-01-07 18:00 | 1 | 1 | 1
2024-01-07 19:00 | 1 | 1 | 1
2024-01-07 20:00 | 1 | 1 | 1
2024-01-07 21:00 | 1 | 1 | 1
2024-01-07 22:00 | 1 | 1 | 1
2024-01-07 23:00 | 1 | 0 | 1

## Store_Power
scenario | cold | medium | warm
name | thermal_storage | thermal_storage | thermal_storage
snapshot
2024-01-01 | -0.44946 | -0.18756 | -0.1831
2024-01-01 01:00 | 0.32886 | 0.32692 | 0.32536
2024-01-01 02:00 | 0.34504 | 0.33995 | 0.3361
2024-01-01 03:00 | 0.23964 | -0.14464 | -0.15092
2024-01-01 04:00 | 0 | -0.1215 | -0.12994
2024-01-01 05:00 | 0 | -0.098729 | -0.10892
2024-01-01 06:00 | 0 | -0.079841 | -0.17681
2024-01-01 07:00 | 0 | -0.066824 | -0.078543
2024-01-01 08:00 | -0.033264 | -0.059782 | -0.071522
2024-01-01 09:00 | -0.02958 | -0.058301 | -0.069571
2024-01-01 10:00 | -0.030181 | -0.060286 | -0.071346
2024-01-01 11:00 | -0.032803 | 0.44057 | -0.075311
2024-01-01 12:00 | -0.035595 | -0.066981 | -0.079237
2024-01-01 13:00 | -0.037799 | -0.068993 | 0.42312
2024-01-01 14:00 | -0.72169 | -0.07047 | 0.42225
2024-01-01 15:00 | -0.039005 | -0.071851 | -0.083297
2024-01-01 16:00 | -0.039348 | -0.07263 | -0.085053
2024-01-01 17:00 | 0.46388 | -0.073883 | -0.087817
2024-01-01 18:00 | 0.45726 | -0.077596 | -0.092824
2024-01-01 19:00 | -0.049216 | -0.084461 | -0.10063
2024-01-01 20:00 | -0.058066 | -0.09459 | -0.11183
2024-01-01 21:00 | -0.069508 | -0.10749 | -0.12631
2024-01-01 22:00 | -0.081239 | 0.38413 | -0.1409
2024-01-01 23:00 | -0.091684 | 0.37365 | -0.15273
2024-01-02 | -0.10062 | -0.13905 | 0.34235
2024-01-02 01:00 | -0.094284 | -0.13192 | 0.34818
2024-01-02 02:00 | -0.083045 | -0.11801 | 0.22361
2024-01-02 03:00 | -0.066094 | -0.097581 | 0
2024-01-02 04:00 | -0.046284 | 0.43064 | -0.60284
2024-01-02 05:00 | -0.026357 | -0.050172 | -0.07473
2024-01-02 06:00 | -0.0087497 | -0.030348 | -0.053765
2024-01-02 07:00 | 0.0047473 | -0.016707 | -0.039323
2024-01-02 08:00 | 0.013185 | -0.0097678 | -0.031914
2024-01-02 09:00 | 0.016735 | -0.0080402 | -0.030705
2024-01-02 10:00 | 0.016383 | -0.0097456 | -0.033576
2024-01-02 11:00 | 0.01365 | -0.013221 | -0.038438
2024-01-02 12:00 | 0.010032 | -0.017326 | -0.04318
2024-01-02 13:00 | 0.0064326 | -0.021282 | -0.046469
2024-01-02 14:00 | 0.0033607 | -0.022818 | -0.047675
2024-01-02 15:00 | 0.00097255 | -0.022395 | -0.046939
2024-01-02 16:00 | -0.00048705 | -0.022115 | -0.045262
2024-01-02 17:00 | -0.0026327 | -0.022459 | 0.46031
2024-01-02 18:00 | -0.0066772 | -0.024765 | 0.45985
2024-01-02 19:00 | -0.013722 | -0.030435 | -0.048593
2024-01-02 20:00 | -0.02474 | -0.040738 | -0.057423
2024-01-02 21:00 | -0.039596 | -0.055311 | -0.070951
2024-01-02 22:00 | -0.055571 | -0.071747 | -0.0864
2024-01-02 23:00 | -0.07033 | -0.087125 | -0.10059
2024-01-03 | -0.083331 | -0.1004 | -0.11299
2024-01-03 01:00 | -0.075161 | -0.093008 | -0.10478
2024-01-03 02:00 | -0.060848 | -0.080182 | -0.30679
2024-01-03 03:00 | -0.04074 | -0.062261 | -0.070994
2024-01-03 04:00 | -0.017988 | -0.04148 | -0.050189
2024-01-03 05:00 | 0.0041513 | -0.021181 | -0.032508
2024-01-03 06:00 | 0.022943 | -0.0039091 | 0.4844
2024-01-03 07:00 | 0.036926 | 0.0078611 | 0.43715
2024-01-03 08:00 | 0.045465 | 0.013534 | -0.012363
2024-01-03 09:00 | 0.048883 | 0.013818 | -0.015902
2024-01-03 10:00 | 0.04799 | 0.0098564 | -0.02241
2024-01-03 11:00 | 0.044385 | 0.0035704 | -0.029495
2024-01-03 12:00 | 0.039262 | -0.0034708 | -0.036254
2024-01-03 13:00 | 0.03375 | -0.029852 | -0.042722
2024-01-03 14:00 | 0.029318 | -0.016748 | -0.04936
2024-01-03 15:00 | 0.026121 | -0.022988 | -0.055418
2024-01-03 16:00 | 0.023107 | -0.028075 | -0.060985
2024-01-03 17:00 | 0.019497 | -0.032822 | -0.066874
2024-01-03 18:00 | 0.014132 | -0.03913 | -0.073626
2024-01-03 19:00 | 0.0062168 | -0.048251 | -0.082872
2024-01-03 20:00 | -0.0050986 | -0.060917 | -0.095935
2024-01-03 21:00 | -0.020122 | -0.077982 | -0.11363
2024-01-03 22:00 | -0.036598 | 0.40684 | -0.13337
2024-01-03 23:00 | -0.051744 | 0.38884 | -0.15043
2024-01-04 | -0.065135 | 0.12184 | 0.34095
2024-01-04 01:00 | -0.056115 | -0.12509 | 0.35021
2024-01-04 02:00 | -0.0394 | -0.11283 | 0.22297
2024-01-04 03:00 | -0.49252 | -0.094692 | -6.163e-33
2024-01-04 04:00 | -0.018989 | -0.073995 | 0
2024-01-04 05:00 | -0.018989 | -0.054151 | -0.54199
2024-01-04 06:00 | -0.018989 | -0.037554 | -0.030284
2024-01-04 07:00 | 0.073532 | -0.026124 | -0.012077
2024-01-04 08:00 | 0.080825 | -0.019908 | 6.2867e-05
2024-01-04 09:00 | 0.08188 | -0.018389 | 0.0076368
2024-01-04 10:00 | 0.07896 | -0.019073 | 0.012249
2024-01-04 11:00 | 0.074246 | -0.02188 | 0.015664
2024-01-04 12:00 | 0.069533 | -0.026331 | 0.019496
2024-01-04 13:00 | 0.065417 | -0.13657 | 0.024271
2024-01-04 14:00 | 0.061881 | -0.035786 | 0.030292
2024-01-04 15:00 | 0.058684 | -0.039026 | 0.036731
2024-01-04 16:00 | 0.056226 | -0.041527 | 0.04329
2024-01-04 17:00 | 0.053432 | -0.043979 | 0.048672
2024-01-04 18:00 | 0.048956 | -0.047547 | 0.051461
2024-01-04 19:00 | 0.031246 | -0.054025 | 0.050486
2024-01-04 20:00 | 0 | -0.064676 | 0.044908
2024-01-04 21:00 | 0 | -0.079369 | 0.034938
2024-01-04 22:00 | -0.0040395 | 0.40878 | 0.023056
2024-01-04 23:00 | -0.020492 | 0.39364 | 0.012
2024-01-05 | -0.033779 | 0.11526 | 0.0032574
2024-01-05 01:00 | -0.02578 | -0.11581 | 0
2024-01-05 02:00 | -0.010428 | -0.10024 | 0
2024-01-05 03:00 | 0.011388 | -0.078228 | 0
2024-01-05 04:00 | -0.87308 | -0.053125 | -0.94946
2024-01-05 05:00 | -0.018989 | -0.028707 | -0.018989
2024-01-05 06:00 | -0.018989 | -0.0084156 | 0.0016809
2024-01-05 07:00 | 0.093507 | 0.0056081 | 0.14541
2024-01-05 08:00 | 0.098448 | 0.012649 | 0.14917
2024-01-05 09:00 | 0.097321 | 0.013701 | 0.14836
2024-01-05 10:00 | 0.092388 | 0.0099077 | 0.14514
2024-01-05 11:00 | 0.085892 | 0.0039663 | 0.14091
2024-01-05 12:00 | 0.079382 | -0.0016402 | 0.13661
2024-01-05 13:00 | 0.073486 | -0.0054052 | -0.77341
2024-01-05 14:00 | 0.068857 | -0.0081232 | 0.12986
2024-01-05 15:00 | 0.065168 | -0.010283 | 0.12731
2024-01-05 16:00 | 0.039039 | -0.01222 | 0.12466
2024-01-05 17:00 | 0.057501 | -0.015351 | 0.12069
2024-01-05 18:00 | 0 | -0.020018 | 0.11439
2024-01-05 19:00 | 0 | -0.026918 | 0.10497
2024-01-05 20:00 | 0 | -0.037898 | 0
2024-01-05 21:00 | 0 | -0.053183 | 0
2024-01-05 22:00 | -0.010582 | -0.070717 | 0
2024-01-05 23:00 | -0.028504 | -0.086598 | 0
2024-01-06 | -0.042282 | -0.099272 | 0
2024-01-06 01:00 | -0.033271 | -0.090008 | 0
2024-01-06 02:00 | -0.016601 | -0.073469 | 0
2024-01-06 03:00 | -0.056593 | -0.050344 | 0
2024-01-06 04:00 | 0.033289 | -0.024145 | -0.10258
2024-01-06 05:00 | 0.059076 | 0.00085759 | 0.10053
2024-01-06 06:00 | 0.079989 | 0.020852 | -0.94946
2024-01-06 07:00 | -0.94946 | 0.033377 | 0.081718
2024-01-06 08:00 | 0.10139 | 0.038671 | 0.13508
2024-01-06 09:00 | 0.1034 | 0.038026 | 0.13712
2024-01-06 10:00 | 0.10185 | 0.034249 | 0.13574
2024-01-06 11:00 | 0.098311 | 0.02819 | 0.13225
2024-01-06 12:00 | 0.094131 | 0.021566 | 0.12779
2024-01-06 13:00 | 0.090704 | 0.016127 | 0.12327
2024-01-06 14:00 | 0.088506 | 0.012595 | -0.45722
2024-01-06 15:00 | 0.0063568 | 0.010662 | 0.11571
2024-01-06 16:00 | 0.086542 | 0.0095227 | 0.11202
2024-01-06 17:00 | 0.084802 | 0.0077177 | 0.10714
2024-01-06 18:00 | 0 | 0.0037036 | 0.10023
2024-01-06 19:00 | -0.060937 | -0.0041732 | 0
2024-01-06 20:00 | 0.059719 | -0.016655 | 0
2024-01-06 21:00 | 0 | -0.034391 | 0
2024-01-06 22:00 | 0 | -0.053969 | 0
2024-01-06 23:00 | 0 | -0.071389 | -0.010697
2024-01-07 | -0.0055217 | -0.085437 | 0.010483
2024-01-07 01:00 | 0.0045116 | -0.076714 | 0
2024-01-07 02:00 | 0.00088166 | -0.060386 | 0
2024-01-07 03:00 | 0 | -0.03777 | 0
2024-01-07 04:00 | -0.94946 | -0.012469 | 0
2024-01-07 05:00 | -0.018989 | 0.011456 | -0.94946
2024-01-07 06:00 | -0.018989 | 0.02967 | 0.0019606
2024-01-07 07:00 | -0.018989 | 0.040393 | 0.13079
2024-01-07 08:00 | 0.13376 | 0.043072 | 0.14119
2024-01-07 09:00 | 0.13274 | 0.040047 | 0.14713
2024-01-07 10:00 | 0.12743 | 0.032542 | 0.14913
2024-01-07 11:00 | 0.11962 | 0.022771 | 0.14872
2024-01-07 12:00 | 0.11128 | 0.012729 | 0.14661
2024-01-07 13:00 | 0.10435 | 0.0045891 | 0
2024-01-07 14:00 | -0.22807 | -0.0015631 | -0.84347
2024-01-07 15:00 | 0.095527 | -0.0066736 | 0.13947
2024-01-07 16:00 | 0.092142 | -0.010713 | 0.13746
2024-01-07 17:00 | 0.087624 | -0.014606 | 0.13525
2024-01-07 18:00 | 0.081234 | -0.020425 | 0.13202
2024-01-07 19:00 | 0 | -0.029214 | 0.12616
2024-01-07 20:00 | 0 | -0.042236 | 0.11661
2024-01-07 21:00 | 0 | -0.059967 | 0
2024-01-07 22:00 | 0 | -0.079977 | 0
2024-01-07 23:00 | 0 | 0.40588 | 0

## Store_Energy_SOC
scenario | cold | medium | warm
name | thermal_storage | thermal_storage | thermal_storage
snapshot
2024-01-01 | 0.94946 | 0.68756 | 0.6831
2024-01-01 01:00 | 0.60161 | 0.34689 | 0.34408
2024-01-01 02:00 | 0.24453 | 0 | 0.0010927
2024-01-01 03:00 | 0 | 0.14464 | 0.15199
2024-01-01 04:00 | 0 | 0.26325 | 0.2789
2024-01-01 05:00 | 0 | 0.35672 | 0.38224
2024-01-01 06:00 | 0 | 0.42942 | 0.55141
2024-01-01 07:00 | 0 | 0.48766 | 0.61892
2024-01-01 08:00 | 0.033264 | 0.53769 | 0.67806
2024-01-01 09:00 | 0.062178 | 0.58523 | 0.73407
2024-01-01 10:00 | 0.091115 | 0.63381 | 0.79074
2024-01-01 11:00 | 0.1221 | 0.18057 | 0.85023
2024-01-01 12:00 | 0.15525 | 0.24394 | 0.91247
2024-01-01 13:00 | 0.18994 | 0.30805 | 0.47109
2024-01-01 14:00 | 0.90784 | 0.37236 | 0.039422
2024-01-01 15:00 | 0.92869 | 0.43676 | 0.12193
2024-01-01 16:00 | 0.94946 | 0.50066 | 0.20454
2024-01-01 17:00 | 0.46659 | 0.56453 | 0.28827
2024-01-01 18:00 | 0 | 0.63083 | 0.37533
2024-01-01 19:00 | 0.049216 | 0.70268 | 0.46846
2024-01-01 20:00 | 0.1063 | 0.78321 | 0.57092
2024-01-01 21:00 | 0.17368 | 0.87504 | 0.68581
2024-01-01 22:00 | 0.25145 | 0.47341 | 0.81299
2024-01-01 23:00 | 0.3381 | 0.090297 | 0.94946
2024-01-02 | 0.43196 | 0.22754 | 0.58812
2024-01-02 01:00 | 0.5176 | 0.35491 | 0.22818
2024-01-02 02:00 | 0.59029 | 0.46582 | 0
2024-01-02 03:00 | 0.64458 | 0.55409 | 0
2024-01-02 04:00 | 0.67798 | 0.11236 | 0.60284
2024-01-02 05:00 | 0.69077 | 0.16028 | 0.66551
2024-01-02 06:00 | 0.68571 | 0.18743 | 0.70597
2024-01-02 07:00 | 0.66725 | 0.20038 | 0.73117
2024-01-02 08:00 | 0.64072 | 0.20614 | 0.74846
2024-01-02 09:00 | 0.61117 | 0.21006 | 0.7642
2024-01-02 10:00 | 0.58256 | 0.21561 | 0.78249
2024-01-02 11:00 | 0.55726 | 0.22452 | 0.80528
2024-01-02 12:00 | 0.53608 | 0.23735 | 0.83235
2024-01-02 13:00 | 0.51893 | 0.25389 | 0.86217
2024-01-02 14:00 | 0.50519 | 0.27163 | 0.89261
2024-01-02 15:00 | 0.49411 | 0.28859 | 0.92169
2024-01-02 16:00 | 0.48472 | 0.30493 | 0.94852
2024-01-02 17:00 | 0.47766 | 0.32129 | 0.46924
2024-01-02 18:00 | 0.47478 | 0.33963 | 0
2024-01-02 19:00 | 0.47901 | 0.36327 | 0.048593
2024-01-02 20:00 | 0.49417 | 0.39675 | 0.10504
2024-01-02 21:00 | 0.52388 | 0.44412 | 0.17389
2024-01-02 22:00 | 0.56897 | 0.50699 | 0.25682
2024-01-02 23:00 | 0.62792 | 0.58397 | 0.35227
2024-01-03 | 0.6987 | 0.67269 | 0.45822
2024-01-03 01:00 | 0.75988 | 0.75225 | 0.55383
2024-01-03 02:00 | 0.80553 | 0.81739 | 0.84954
2024-01-03 03:00 | 0.83016 | 0.8633 | 0.90355
2024-01-03 04:00 | 0.83155 | 0.88751 | 0.93567
2024-01-03 05:00 | 0.81076 | 0.89094 | 0.94946
2024-01-03 06:00 | 0.77161 | 0.87703 | 0.44607
2024-01-03 07:00 | 0.71925 | 0.85163 | 0
2024-01-03 08:00 | 0.6594 | 0.82107 | 0.012363
2024-01-03 09:00 | 0.59733 | 0.79083 | 0.028018
2024-01-03 10:00 | 0.53739 | 0.76515 | 0.049868
2024-01-03 11:00 | 0.48226 | 0.74628 | 0.078366
2024-01-03 12:00 | 0.43335 | 0.73482 | 0.11305
2024-01-03 13:00 | 0.39093 | 0.74998 | 0.15351
2024-01-03 14:00 | 0.3538 | 0.75173 | 0.1998
2024-01-03 15:00 | 0.3206 | 0.75968 | 0.25122
2024-01-03 16:00 | 0.29108 | 0.77256 | 0.30719
2024-01-03 17:00 | 0.26576 | 0.78993 | 0.36792
2024-01-03 18:00 | 0.24631 | 0.81326 | 0.43418
2024-01-03 19:00 | 0.23517 | 0.84525 | 0.50837
2024-01-03 20:00 | 0.23556 | 0.88926 | 0.59414
2024-01-03 21:00 | 0.25098 | 0.94946 | 0.69588
2024-01-03 22:00 | 0.28255 | 0.52363 | 0.81534
2024-01-03 23:00 | 0.32865 | 0.12432 | 0.94946
2024-01-04 | 0.38721 | 0 | 0.58952
2024-01-04 01:00 | 0.43558 | 0.12509 | 0.22753
2024-01-04 02:00 | 0.46627 | 0.23541 | 0
2024-01-04 03:00 | 0.94946 | 0.32539 | 0
2024-01-04 04:00 | 0.94946 | 0.39288 | 0
2024-01-04 05:00 | 0.94946 | 0.43917 | 0.54199
2024-01-04 06:00 | 0.94946 | 0.46794 | 0.56144
2024-01-04 07:00 | 0.85694 | 0.48471 | 0.56229
2024-01-04 08:00 | 0.75897 | 0.49492 | 0.55098
2024-01-04 09:00 | 0.66192 | 0.50341 | 0.53232
2024-01-04 10:00 | 0.56972 | 0.51242 | 0.50943
2024-01-04 11:00 | 0.48408 | 0.52405 | 0.48357
2024-01-04 12:00 | 0.40486 | 0.5399 | 0.45441
2024-01-04 13:00 | 0.33135 | 0.66568 | 0.42105
2024-01-04 14:00 | 0.26284 | 0.68815 | 0.38233
2024-01-04 15:00 | 0.1989 | 0.71341 | 0.33796
2024-01-04 16:00 | 0.1387 | 0.74067 | 0.28791
2024-01-04 17:00 | 0.082489 | 0.76983 | 0.23348
2024-01-04 18:00 | 0.031883 | 0.80198 | 0.17735
2024-01-04 19:00 | 0 | 0.83997 | 0.12331
2024-01-04 20:00 | 0 | 0.88785 | 0.075939
2024-01-04 21:00 | 0 | 0.94946 | 0.039483
2024-01-04 22:00 | 0.0040395 | 0.52169 | 0.015637
2024-01-04 23:00 | 0.02445 | 0.11762 | 0.0033239
2024-01-05 | 0.05774 | 0 | 0
2024-01-05 01:00 | 0.082365 | 0.11581 | 0
2024-01-05 02:00 | 0.091145 | 0.21373 | 0
2024-01-05 03:00 | 0.077934 | 0.28769 | 0
2024-01-05 04:00 | 0.94946 | 0.33506 | 0.94946
2024-01-05 05:00 | 0.94946 | 0.35706 | 0.94946
2024-01-05 06:00 | 0.94946 | 0.35834 | 0.92879
2024-01-05 07:00 | 0.83696 | 0.34556 | 0.7648
2024-01-05 08:00 | 0.72178 | 0.326 | 0.60034
2024-01-05 09:00 | 0.61002 | 0.30578 | 0.43997
2024-01-05 10:00 | 0.50543 | 0.28976 | 0.28603
2024-01-05 11:00 | 0.40943 | 0.28 | 0.1394
2024-01-05 12:00 | 0.32186 | 0.27604 | 0
2024-01-05 13:00 | 0.24194 | 0.27592 | 0.77341
2024-01-05 14:00 | 0.16824 | 0.27853 | 0.62809
2024-01-05 15:00 | 0.099708 | 0.28324 | 0.48821
2024-01-05 16:00 | 0.058675 | 0.28979 | 0.35379
2024-01-05 17:00 | 0 | 0.29935 | 0.22602
2024-01-05 18:00 | 0 | 0.31338 | 0.10711
2024-01-05 19:00 | 0 | 0.33403 | 0
2024-01-05 20:00 | 0 | 0.36525 | 0
2024-01-05 21:00 | 0 | 0.41113 | 0
2024-01-05 22:00 | 0.010582 | 0.47362 | 0
2024-01-05 23:00 | 0.038875 | 0.55075 | 0
2024-01-06 | 0.080379 | 0.639 | 0
2024-01-06 01:00 | 0.11204 | 0.71623 | 0
2024-01-06 02:00 | 0.1264 | 0.77538 | 0
2024-01-06 03:00 | 0.18047 | 0.81021 | 0
2024-01-06 04:00 | 0.14357 | 0.81816 | 0.10258
2024-01-06 05:00 | 0.081621 | 0.80093 | 0
2024-01-06 06:00 | 0 | 0.76406 | 0.94946
2024-01-06 07:00 | 0.94946 | 0.71541 | 0.84875
2024-01-06 08:00 | 0.82908 | 0.66243 | 0.6967
2024-01-06 09:00 | 0.7091 | 0.61115 | 0.54564
2024-01-06 10:00 | 0.59307 | 0.56468 | 0.39899
2024-01-06 11:00 | 0.48289 | 0.5252 | 0.25875
2024-01-06 12:00 | 0.37911 | 0.49313 | 0.12579
2024-01-06 13:00 | 0.28082 | 0.46714 | 0
2024-01-06 14:00 | 0.1867 | 0.4452 | 0.45722
2024-01-06 15:00 | 0.17661 | 0.42563 | 0.33236
2024-01-06 16:00 | 0.086533 | 0.4076 | 0.2137
2024-01-06 17:00 | 0 | 0.39173 | 0.10228
2024-01-06 18:00 | 0 | 0.38019 | 0
2024-01-06 19:00 | 0.060937 | 0.37676 | 0
2024-01-06 20:00 | 0 | 0.38588 | 0
2024-01-06 21:00 | 0 | 0.41255 | 0
2024-01-06 22:00 | 0 | 0.45827 | 0
2024-01-06 23:00 | 0 | 0.52049 | 0.010697
2024-01-07 | 0.0055217 | 0.59552 | 0
2024-01-07 01:00 | 0.00089965 | 0.66033 | 0
2024-01-07 02:00 | 0 | 0.7075 | 0
2024-01-07 03:00 | 0 | 0.73112 | 0
2024-01-07 04:00 | 0.94946 | 0.72897 | 0
2024-01-07 05:00 | 0.94946 | 0.70294 | 0.94946
2024-01-07 06:00 | 0.94946 | 0.65921 | 0.92851
2024-01-07 07:00 | 0.94946 | 0.60563 | 0.77915
2024-01-07 08:00 | 0.79671 | 0.55045 | 0.62238
2024-01-07 09:00 | 0.64804 | 0.49939 | 0.46279
2024-01-07 10:00 | 0.50765 | 0.45686 | 0.30441
2024-01-07 11:00 | 0.37788 | 0.42495 | 0.1496
2024-01-07 12:00 | 0.25904 | 0.40372 | 0
2024-01-07 13:00 | 0.14951 | 0.39106 | 0
2024-01-07 14:00 | 0.37459 | 0.3848 | 0.84347
2024-01-07 15:00 | 0.27157 | 0.38378 | 0.68714
2024-01-07 16:00 | 0.174 | 0.38682 | 0.53594
2024-01-07 17:00 | 0.082892 | 0.39369 | 0.38997
2024-01-07 18:00 | 0 | 0.40624 | 0.25015
2024-01-07 19:00 | 0 | 0.42733 | 0.11899
2024-01-07 20:00 | 0 | 0.46102 | 0
2024-01-07 21:00 | 0 | 0.51177 | 0
2024-01-07 22:00 | 0 | 0.58151 | 0
2024-01-07 23:00 | 0 | 0.164 | 0

## Load_Demand
scenario | cold | medium | warm
name | heat_demand | heat_demand | heat_demand
snapshot
2024-01-01 | 0.32121 | 0.32121 | 0.32121
2024-01-01 01:00 | 0.32886 | 0.32692 | 0.32536
2024-01-01 02:00 | 0.34504 | 0.33995 | 0.3361
2024-01-01 03:00 | 0.36843 | 0.35967 | 0.35339
2024-01-01 04:00 | 0.39545 | 0.3828 | 0.37436
2024-01-01 05:00 | 0.42194 | 0.40558 | 0.39538
2024-01-01 06:00 | 0.44472 | 0.42447 | 0.41317
2024-01-01 07:00 | 0.46124 | 0.43748 | 0.42576
2024-01-01 08:00 | 0.47104 | 0.44452 | 0.43278
2024-01-01 09:00 | 0.47472 | 0.446 | 0.43473
2024-01-01 10:00 | 0.47412 | 0.44402 | 0.43296
2024-01-01 11:00 | 0.4715 | 0.44057 | 0.429
2024-01-01 12:00 | 0.46871 | 0.43732 | 0.42507
2024-01-01 13:00 | 0.4665 | 0.43531 | 0.42312
2024-01-01 14:00 | 0.46548 | 0.43384 | 0.42225
2024-01-01 15:00 | 0.4653 | 0.43246 | 0.42101
2024-01-01 16:00 | 0.46496 | 0.43168 | 0.41925
2024-01-01 17:00 | 0.46388 | 0.43042 | 0.41649
2024-01-01 18:00 | 0.4608 | 0.42671 | 0.41148
2024-01-01 19:00 | 0.45509 | 0.41985 | 0.40367
2024-01-01 20:00 | 0.44624 | 0.40972 | 0.39248
2024-01-01 21:00 | 0.4348 | 0.39681 | 0.378
2024-01-01 22:00 | 0.42307 | 0.38413 | 0.36341
2024-01-01 23:00 | 0.41262 | 0.37365 | 0.35158
2024-01-02 | 0.40369 | 0.36525 | 0.34235
2024-01-02 01:00 | 0.41002 | 0.37239 | 0.34818
2024-01-02 02:00 | 0.42126 | 0.3863 | 0.36049
2024-01-02 03:00 | 0.43821 | 0.40672 | 0.38023
2024-01-02 04:00 | 0.45802 | 0.43064 | 0.40484
2024-01-02 05:00 | 0.47795 | 0.45413 | 0.42958
2024-01-02 06:00 | 0.49555 | 0.47396 | 0.45054
2024-01-02 07:00 | 0.50905 | 0.4876 | 0.46498
2024-01-02 08:00 | 0.51749 | 0.49454 | 0.47239
2024-01-02 09:00 | 0.52104 | 0.49627 | 0.4736
2024-01-02 10:00 | 0.52069 | 0.49456 | 0.47073
2024-01-02 11:00 | 0.51795 | 0.49108 | 0.46587
2024-01-02 12:00 | 0.51434 | 0.48698 | 0.46113
2024-01-02 13:00 | 0.51074 | 0.48302 | 0.45784
2024-01-02 14:00 | 0.50767 | 0.48149 | 0.45663
2024-01-02 15:00 | 0.50528 | 0.48191 | 0.45737
2024-01-02 16:00 | 0.50382 | 0.48219 | 0.45904
2024-01-02 17:00 | 0.50167 | 0.48185 | 0.46031
2024-01-02 18:00 | 0.49763 | 0.47954 | 0.45985
2024-01-02 19:00 | 0.49058 | 0.47387 | 0.45571
2024-01-02 20:00 | 0.47956 | 0.46357 | 0.44688
2024-01-02 21:00 | 0.46471 | 0.44899 | 0.43335
2024-01-02 22:00 | 0.44873 | 0.43256 | 0.41791
2024-01-02 23:00 | 0.43397 | 0.41718 | 0.40372
2024-01-03 | 0.42097 | 0.4039 | 0.39131
2024-01-03 01:00 | 0.42914 | 0.4113 | 0.39952
2024-01-03 02:00 | 0.44345 | 0.42412 | 0.41394
2024-01-03 03:00 | 0.46356 | 0.44204 | 0.43331
2024-01-03 04:00 | 0.48632 | 0.46283 | 0.45412
2024-01-03 05:00 | 0.50845 | 0.48312 | 0.4718
2024-01-03 06:00 | 0.52724 | 0.5004 | 0.4844
2024-01-03 07:00 | 0.54123 | 0.51217 | 0.49096
2024-01-03 08:00 | 0.54977 | 0.51784 | 0.49194
2024-01-03 09:00 | 0.55318 | 0.51812 | 0.4884
2024-01-03 10:00 | 0.55229 | 0.51416 | 0.48189
2024-01-03 11:00 | 0.54869 | 0.50788 | 0.47481
2024-01-03 12:00 | 0.54357 | 0.50084 | 0.46805
2024-01-03 13:00 | 0.53805 | 0.49393 | 0.46158
2024-01-03 14:00 | 0.53362 | 0.48756 | 0.45494
2024-01-03 15:00 | 0.53042 | 0.48132 | 0.44889
2024-01-03 16:00 | 0.52741 | 0.47623 | 0.44332
2024-01-03 17:00 | 0.5238 | 0.47148 | 0.43743
2024-01-03 18:00 | 0.51844 | 0.46518 | 0.43068
2024-01-03 19:00 | 0.51052 | 0.45606 | 0.42143
2024-01-03 20:00 | 0.4992 | 0.44339 | 0.40837
2024-01-03 21:00 | 0.48418 | 0.42632 | 0.39068
2024-01-03 22:00 | 0.46771 | 0.40684 | 0.37094
2024-01-03 23:00 | 0.45256 | 0.38884 | 0.35388
2024-01-04 | 0.43917 | 0.37307 | 0.34095
2024-01-04 01:00 | 0.44819 | 0.37922 | 0.35021
2024-01-04 02:00 | 0.4649 | 0.39148 | 0.36708
2024-01-04 03:00 | 0.48795 | 0.40961 | 0.39176
2024-01-04 04:00 | 0.51469 | 0.43031 | 0.42082
2024-01-04 05:00 | 0.54117 | 0.45015 | 0.44951
2024-01-04 06:00 | 0.56308 | 0.46675 | 0.47402
2024-01-04 07:00 | 0.57783 | 0.47818 | 0.49222
2024-01-04 08:00 | 0.58512 | 0.4844 | 0.50436
2024-01-04 09:00 | 0.58618 | 0.48592 | 0.51193
2024-01-04 10:00 | 0.58326 | 0.48523 | 0.51654
2024-01-04 11:00 | 0.57855 | 0.48243 | 0.51996
2024-01-04 12:00 | 0.57383 | 0.47797 | 0.52379
2024-01-04 13:00 | 0.56972 | 0.47294 | 0.52857
2024-01-04 14:00 | 0.56618 | 0.46852 | 0.53459
2024-01-04 15:00 | 0.56299 | 0.46528 | 0.54103
2024-01-04 16:00 | 0.56053 | 0.46278 | 0.54759
2024-01-04 17:00 | 0.55773 | 0.46033 | 0.55297
2024-01-04 18:00 | 0.55326 | 0.45676 | 0.55576
2024-01-04 19:00 | 0.54583 | 0.45028 | 0.55478
2024-01-04 20:00 | 0.53449 | 0.43963 | 0.5492
2024-01-04 21:00 | 0.51846 | 0.42494 | 0.53923
2024-01-04 22:00 | 0.50026 | 0.40878 | 0.52735
2024-01-04 23:00 | 0.48381 | 0.39364 | 0.51629
2024-01-05 | 0.47052 | 0.38019 | 0.50755
2024-01-05 01:00 | 0.47852 | 0.3885 | 0.52219
2024-01-05 02:00 | 0.49387 | 0.40406 | 0.54319
2024-01-05 03:00 | 0.51569 | 0.42608 | 0.56901
2024-01-05 04:00 | 0.54093 | 0.45118 | 0.59618
2024-01-05 05:00 | 0.56555 | 0.4756 | 0.62055
2024-01-05 06:00 | 0.58538 | 0.49589 | 0.63887
2024-01-05 07:00 | 0.59781 | 0.50991 | 0.64971
2024-01-05 08:00 | 0.60275 | 0.51695 | 0.65346
2024-01-05 09:00 | 0.60162 | 0.51801 | 0.65266
2024-01-05 10:00 | 0.59669 | 0.51421 | 0.64944
2024-01-05 11:00 | 0.59019 | 0.50827 | 0.6452
2024-01-05 12:00 | 0.58368 | 0.50267 | 0.6409
2024-01-05 13:00 | 0.57779 | 0.4989 | 0.63722
2024-01-05 14:00 | 0.57316 | 0.49618 | 0.63415
2024-01-05 15:00 | 0.56947 | 0.49402 | 0.63161
2024-01-05 16:00 | 0.56591 | 0.49209 | 0.62896
2024-01-05 17:00 | 0.5618 | 0.48895 | 0.62499
2024-01-05 18:00 | 0.55596 | 0.48429 | 0.61869
2024-01-05 19:00 | 0.5467 | 0.47739 | 0.60926
2024-01-05 20:00 | 0.53283 | 0.46641 | 0.59596
2024-01-05 21:00 | 0.51414 | 0.45112 | 0.57836
2024-01-05 22:00 | 0.49372 | 0.43359 | 0.55899
2024-01-05 23:00 | 0.4758 | 0.41771 | 0.54152
2024-01-06 | 0.46202 | 0.40503 | 0.52809
2024-01-06 01:00 | 0.47103 | 0.4143 | 0.53475
2024-01-06 02:00 | 0.4877 | 0.43084 | 0.54732
2024-01-06 03:00 | 0.51097 | 0.45396 | 0.56503
2024-01-06 04:00 | 0.53759 | 0.48016 | 0.58519
2024-01-06 05:00 | 0.56338 | 0.50516 | 0.60482
2024-01-06 06:00 | 0.58429 | 0.52516 | 0.6212
2024-01-06 07:00 | 0.59828 | 0.53768 | 0.6328
2024-01-06 08:00 | 0.60568 | 0.54297 | 0.63937
2024-01-06 09:00 | 0.6077 | 0.54233 | 0.64142
2024-01-06 10:00 | 0.60615 | 0.53855 | 0.64004
2024-01-06 11:00 | 0.60261 | 0.5325 | 0.63655
2024-01-06 12:00 | 0.59843 | 0.52587 | 0.63209
2024-01-06 13:00 | 0.595 | 0.52043 | 0.62757
2024-01-06 14:00 | 0.5928 | 0.5169 | 0.62343
2024-01-06 15:00 | 0.59183 | 0.51497 | 0.62001
2024-01-06 16:00 | 0.59084 | 0.51383 | 0.61631
2024-01-06 17:00 | 0.5891 | 0.51202 | 0.61144
2024-01-06 18:00 | 0.58479 | 0.50801 | 0.60453
2024-01-06 19:00 | 0.57667 | 0.50013 | 0.59481
2024-01-06 20:00 | 0.56402 | 0.48765 | 0.58152
2024-01-06 21:00 | 0.54694 | 0.46991 | 0.56447
2024-01-06 22:00 | 0.52838 | 0.45034 | 0.54615
2024-01-06 23:00 | 0.51189 | 0.43292 | 0.52928
2024-01-07 | 0.49878 | 0.41887 | 0.51478
2024-01-07 01:00 | 0.50881 | 0.42759 | 0.52204
2024-01-07 02:00 | 0.52615 | 0.44392 | 0.53611
2024-01-07 03:00 | 0.54964 | 0.46653 | 0.55582
2024-01-07 04:00 | 0.5758 | 0.49184 | 0.57854
2024-01-07 05:00 | 0.60073 | 0.51576 | 0.60099
2024-01-07 06:00 | 0.62056 | 0.53397 | 0.62024
2024-01-07 07:00 | 0.63302 | 0.5447 | 0.63508
2024-01-07 08:00 | 0.63806 | 0.54738 | 0.64547
2024-01-07 09:00 | 0.63703 | 0.54435 | 0.65142
2024-01-07 10:00 | 0.63173 | 0.53685 | 0.65342
2024-01-07 11:00 | 0.62392 | 0.52708 | 0.65301
2024-01-07 12:00 | 0.61558 | 0.51703 | 0.6509
2024-01-07 13:00 | 0.60866 | 0.5089 | 0.64831
2024-01-07 14:00 | 0.60359 | 0.50274 | 0.64592
2024-01-07 15:00 | 0.59983 | 0.49763 | 0.64375
2024-01-07 16:00 | 0.59644 | 0.49359 | 0.64174
2024-01-07 17:00 | 0.59192 | 0.4897 | 0.63953
2024-01-07 18:00 | 0.58553 | 0.48388 | 0.6363
2024-01-07 19:00 | 0.57585 | 0.47509 | 0.63044
2024-01-07 20:00 | 0.56181 | 0.46207 | 0.62089
2024-01-07 21:00 | 0.54329 | 0.44434 | 0.60777
2024-01-07 22:00 | 0.5231 | 0.42433 | 0.59343
2024-01-07 23:00 | 0.50538 | 0.40588 | 0.58057

## Load_P_Set
scenario | cold | medium | warm
name | heat_demand | heat_demand | heat_demand
snapshot
2024-01-01 | 0.32121 | 0.32121 | 0.32121
2024-01-01 01:00 | 0.32886 | 0.32692 | 0.32536
2024-01-01 02:00 | 0.34504 | 0.33995 | 0.3361
2024-01-01 03:00 | 0.36843 | 0.35967 | 0.35339
2024-01-01 04:00 | 0.39545 | 0.3828 | 0.37436
2024-01-01 05:00 | 0.42194 | 0.40558 | 0.39538
2024-01-01 06:00 | 0.44472 | 0.42447 | 0.41317
2024-01-01 07:00 | 0.46124 | 0.43748 | 0.42576
2024-01-01 08:00 | 0.47104 | 0.44452 | 0.43278
2024-01-01 09:00 | 0.47472 | 0.446 | 0.43473
2024-01-01 10:00 | 0.47412 | 0.44402 | 0.43296
2024-01-01 11:00 | 0.4715 | 0.44057 | 0.429
2024-01-01 12:00 | 0.46871 | 0.43732 | 0.42507
2024-01-01 13:00 | 0.4665 | 0.43531 | 0.42312
2024-01-01 14:00 | 0.46548 | 0.43384 | 0.42225
2024-01-01 15:00 | 0.4653 | 0.43246 | 0.42101
2024-01-01 16:00 | 0.46496 | 0.43168 | 0.41925
2024-01-01 17:00 | 0.46388 | 0.43042 | 0.41649
2024-01-01 18:00 | 0.4608 | 0.42671 | 0.41148
2024-01-01 19:00 | 0.45509 | 0.41985 | 0.40367
2024-01-01 20:00 | 0.44624 | 0.40972 | 0.39248
2024-01-01 21:00 | 0.4348 | 0.39681 | 0.378
2024-01-01 22:00 | 0.42307 | 0.38413 | 0.36341
2024-01-01 23:00 | 0.41262 | 0.37365 | 0.35158
2024-01-02 | 0.40369 | 0.36525 | 0.34235
2024-01-02 01:00 | 0.41002 | 0.37239 | 0.34818
2024-01-02 02:00 | 0.42126 | 0.3863 | 0.36049
2024-01-02 03:00 | 0.43821 | 0.40672 | 0.38023
2024-01-02 04:00 | 0.45802 | 0.43064 | 0.40484
2024-01-02 05:00 | 0.47795 | 0.45413 | 0.42958
2024-01-02 06:00 | 0.49555 | 0.47396 | 0.45054
2024-01-02 07:00 | 0.50905 | 0.4876 | 0.46498
2024-01-02 08:00 | 0.51749 | 0.49454 | 0.47239
2024-01-02 09:00 | 0.52104 | 0.49627 | 0.4736
2024-01-02 10:00 | 0.52069 | 0.49456 | 0.47073
2024-01-02 11:00 | 0.51795 | 0.49108 | 0.46587
2024-01-02 12:00 | 0.51434 | 0.48698 | 0.46113
2024-01-02 13:00 | 0.51074 | 0.48302 | 0.45784
2024-01-02 14:00 | 0.50767 | 0.48149 | 0.45663
2024-01-02 15:00 | 0.50528 | 0.48191 | 0.45737
2024-01-02 16:00 | 0.50382 | 0.48219 | 0.45904
2024-01-02 17:00 | 0.50167 | 0.48185 | 0.46031
2024-01-02 18:00 | 0.49763 | 0.47954 | 0.45985
2024-01-02 19:00 | 0.49058 | 0.47387 | 0.45571
2024-01-02 20:00 | 0.47956 | 0.46357 | 0.44688
2024-01-02 21:00 | 0.46471 | 0.44899 | 0.43335
2024-01-02 22:00 | 0.44873 | 0.43256 | 0.41791
2024-01-02 23:00 | 0.43397 | 0.41718 | 0.40372
2024-01-03 | 0.42097 | 0.4039 | 0.39131
2024-01-03 01:00 | 0.42914 | 0.4113 | 0.39952
2024-01-03 02:00 | 0.44345 | 0.42412 | 0.41394
2024-01-03 03:00 | 0.46356 | 0.44204 | 0.43331
2024-01-03 04:00 | 0.48632 | 0.46283 | 0.45412
2024-01-03 05:00 | 0.50845 | 0.48312 | 0.4718
2024-01-03 06:00 | 0.52724 | 0.5004 | 0.4844
2024-01-03 07:00 | 0.54123 | 0.51217 | 0.49096
2024-01-03 08:00 | 0.54977 | 0.51784 | 0.49194
2024-01-03 09:00 | 0.55318 | 0.51812 | 0.4884
2024-01-03 10:00 | 0.55229 | 0.51416 | 0.48189
2024-01-03 11:00 | 0.54869 | 0.50788 | 0.47481
2024-01-03 12:00 | 0.54357 | 0.50084 | 0.46805
2024-01-03 13:00 | 0.53805 | 0.49393 | 0.46158
2024-01-03 14:00 | 0.53362 | 0.48756 | 0.45494
2024-01-03 15:00 | 0.53042 | 0.48132 | 0.44889
2024-01-03 16:00 | 0.52741 | 0.47623 | 0.44332
2024-01-03 17:00 | 0.5238 | 0.47148 | 0.43743
2024-01-03 18:00 | 0.51844 | 0.46518 | 0.43068
2024-01-03 19:00 | 0.51052 | 0.45606 | 0.42143
2024-01-03 20:00 | 0.4992 | 0.44339 | 0.40837
2024-01-03 21:00 | 0.48418 | 0.42632 | 0.39068
2024-01-03 22:00 | 0.46771 | 0.40684 | 0.37094
2024-01-03 23:00 | 0.45256 | 0.38884 | 0.35388
2024-01-04 | 0.43917 | 0.37307 | 0.34095
2024-01-04 01:00 | 0.44819 | 0.37922 | 0.35021
2024-01-04 02:00 | 0.4649 | 0.39148 | 0.36708
2024-01-04 03:00 | 0.48795 | 0.40961 | 0.39176
2024-01-04 04:00 | 0.51469 | 0.43031 | 0.42082
2024-01-04 05:00 | 0.54117 | 0.45015 | 0.44951
2024-01-04 06:00 | 0.56308 | 0.46675 | 0.47402
2024-01-04 07:00 | 0.57783 | 0.47818 | 0.49222
2024-01-04 08:00 | 0.58512 | 0.4844 | 0.50436
2024-01-04 09:00 | 0.58618 | 0.48592 | 0.51193
2024-01-04 10:00 | 0.58326 | 0.48523 | 0.51654
2024-01-04 11:00 | 0.57855 | 0.48243 | 0.51996
2024-01-04 12:00 | 0.57383 | 0.47797 | 0.52379
2024-01-04 13:00 | 0.56972 | 0.47294 | 0.52857
2024-01-04 14:00 | 0.56618 | 0.46852 | 0.53459
2024-01-04 15:00 | 0.56299 | 0.46528 | 0.54103
2024-01-04 16:00 | 0.56053 | 0.46278 | 0.54759
2024-01-04 17:00 | 0.55773 | 0.46033 | 0.55297
2024-01-04 18:00 | 0.55326 | 0.45676 | 0.55576
2024-01-04 19:00 | 0.54583 | 0.45028 | 0.55478
2024-01-04 20:00 | 0.53449 | 0.43963 | 0.5492
2024-01-04 21:00 | 0.51846 | 0.42494 | 0.53923
2024-01-04 22:00 | 0.50026 | 0.40878 | 0.52735
2024-01-04 23:00 | 0.48381 | 0.39364 | 0.51629
2024-01-05 | 0.47052 | 0.38019 | 0.50755
2024-01-05 01:00 | 0.47852 | 0.3885 | 0.52219
2024-01-05 02:00 | 0.49387 | 0.40406 | 0.54319
2024-01-05 03:00 | 0.51569 | 0.42608 | 0.56901
2024-01-05 04:00 | 0.54093 | 0.45118 | 0.59618
2024-01-05 05:00 | 0.56555 | 0.4756 | 0.62055
2024-01-05 06:00 | 0.58538 | 0.49589 | 0.63887
2024-01-05 07:00 | 0.59781 | 0.50991 | 0.64971
2024-01-05 08:00 | 0.60275 | 0.51695 | 0.65346
2024-01-05 09:00 | 0.60162 | 0.51801 | 0.65266
2024-01-05 10:00 | 0.59669 | 0.51421 | 0.64944
2024-01-05 11:00 | 0.59019 | 0.50827 | 0.6452
2024-01-05 12:00 | 0.58368 | 0.50267 | 0.6409
2024-01-05 13:00 | 0.57779 | 0.4989 | 0.63722
2024-01-05 14:00 | 0.57316 | 0.49618 | 0.63415
2024-01-05 15:00 | 0.56947 | 0.49402 | 0.63161
2024-01-05 16:00 | 0.56591 | 0.49209 | 0.62896
2024-01-05 17:00 | 0.5618 | 0.48895 | 0.62499
2024-01-05 18:00 | 0.55596 | 0.48429 | 0.61869
2024-01-05 19:00 | 0.5467 | 0.47739 | 0.60926
2024-01-05 20:00 | 0.53283 | 0.46641 | 0.59596
2024-01-05 21:00 | 0.51414 | 0.45112 | 0.57836
2024-01-05 22:00 | 0.49372 | 0.43359 | 0.55899
2024-01-05 23:00 | 0.4758 | 0.41771 | 0.54152
2024-01-06 | 0.46202 | 0.40503 | 0.52809
2024-01-06 01:00 | 0.47103 | 0.4143 | 0.53475
2024-01-06 02:00 | 0.4877 | 0.43084 | 0.54732
2024-01-06 03:00 | 0.51097 | 0.45396 | 0.56503
2024-01-06 04:00 | 0.53759 | 0.48016 | 0.58519
2024-01-06 05:00 | 0.56338 | 0.50516 | 0.60482
2024-01-06 06:00 | 0.58429 | 0.52516 | 0.6212
2024-01-06 07:00 | 0.59828 | 0.53768 | 0.6328
2024-01-06 08:00 | 0.60568 | 0.54297 | 0.63937
2024-01-06 09:00 | 0.6077 | 0.54233 | 0.64142
2024-01-06 10:00 | 0.60615 | 0.53855 | 0.64004
2024-01-06 11:00 | 0.60261 | 0.5325 | 0.63655
2024-01-06 12:00 | 0.59843 | 0.52587 | 0.63209
2024-01-06 13:00 | 0.595 | 0.52043 | 0.62757
2024-01-06 14:00 | 0.5928 | 0.5169 | 0.62343
2024-01-06 15:00 | 0.59183 | 0.51497 | 0.62001
2024-01-06 16:00 | 0.59084 | 0.51383 | 0.61631
2024-01-06 17:00 | 0.5891 | 0.51202 | 0.61144
2024-01-06 18:00 | 0.58479 | 0.50801 | 0.60453
2024-01-06 19:00 | 0.57667 | 0.50013 | 0.59481
2024-01-06 20:00 | 0.56402 | 0.48765 | 0.58152
2024-01-06 21:00 | 0.54694 | 0.46991 | 0.56447
2024-01-06 22:00 | 0.52838 | 0.45034 | 0.54615
2024-01-06 23:00 | 0.51189 | 0.43292 | 0.52928
2024-01-07 | 0.49878 | 0.41887 | 0.51478
2024-01-07 01:00 | 0.50881 | 0.42759 | 0.52204
2024-01-07 02:00 | 0.52615 | 0.44392 | 0.53611
2024-01-07 03:00 | 0.54964 | 0.46653 | 0.55582
2024-01-07 04:00 | 0.5758 | 0.49184 | 0.57854
2024-01-07 05:00 | 0.60073 | 0.51576 | 0.60099
2024-01-07 06:00 | 0.62056 | 0.53397 | 0.62024
2024-01-07 07:00 | 0.63302 | 0.5447 | 0.63508
2024-01-07 08:00 | 0.63806 | 0.54738 | 0.64547
2024-01-07 09:00 | 0.63703 | 0.54435 | 0.65142
2024-01-07 10:00 | 0.63173 | 0.53685 | 0.65342
2024-01-07 11:00 | 0.62392 | 0.52708 | 0.65301
2024-01-07 12:00 | 0.61558 | 0.51703 | 0.6509
2024-01-07 13:00 | 0.60866 | 0.5089 | 0.64831
2024-01-07 14:00 | 0.60359 | 0.50274 | 0.64592
2024-01-07 15:00 | 0.59983 | 0.49763 | 0.64375
2024-01-07 16:00 | 0.59644 | 0.49359 | 0.64174
2024-01-07 17:00 | 0.59192 | 0.4897 | 0.63953
2024-01-07 18:00 | 0.58553 | 0.48388 | 0.6363
2024-01-07 19:00 | 0.57585 | 0.47509 | 0.63044
2024-01-07 20:00 | 0.56181 | 0.46207 | 0.62089
2024-01-07 21:00 | 0.54329 | 0.44434 | 0.60777
2024-01-07 22:00 | 0.5231 | 0.42433 | 0.59343
2024-01-07 23:00 | 0.50538 | 0.40588 | 0.58057

## Input_COLD
snapshot | heat_demand_mw | temp_supply | temp_return | temp_ambient | electricity_price | cop
2024-01-01 | 0.32121 | 72.0086 | 52.3451 | 3.6965 | 50.87 | 2.8017
2024-01-01 01:00 | 0.32886 | 71.9845 | 52.1404 | 3.673 | 48.19 | 2.8017
2024-01-01 02:00 | 0.34504 | 72.0392 | 51.8438 | 3.629 | 44.68 | 2.8017
2024-01-01 03:00 | 0.36843 | 72.1735 | 51.5149 | 3.4746 | 42.92 | 2.8017
2024-01-01 04:00 | 0.39545 | 72.3608 | 51.2116 | 3.4036 | 40.39 | 2.8017
2024-01-01 05:00 | 0.42194 | 72.5663 | 50.9749 | 3.2694 | 40.2 | 2.8017
2024-01-01 06:00 | 0.44472 | 72.7607 | 50.8151 | 3.2679 | 39.63 | 2.8017
2024-01-01 07:00 | 0.46124 | 72.917 | 50.7286 | 3.0901 | 40.09 | 2.8017
2024-01-01 08:00 | 0.47104 | 73.0245 | 50.6918 | 2.9844 | 41.27 | 2.8017
2024-01-01 09:00 | 0.47472 | 73.0819 | 50.6873 | 3.0114 | 44.88 | 2.8017
2024-01-01 10:00 | 0.47412 | 73.1027 | 50.7001 | 3.2301 | 45 | 2.8017
2024-01-01 11:00 | 0.4715 | 73.1033 | 50.7195 | 3.5533 | 47.2 | 2.8017
2024-01-01 12:00 | 0.46871 | 73.0985 | 50.7386 | 3.8862 | 50.78 | 2.8017
2024-01-01 13:00 | 0.4665 | 73.0946 | 50.758 | 4.128 | 45.49 | 2.8017
2024-01-01 14:00 | 0.46548 | 73.095 | 50.7728 | 4.291 | 44.73 | 2.8017
2024-01-01 15:00 | 0.4653 | 73.1 | 50.7865 | 4.3351 | 46.59 | 2.8017
2024-01-01 16:00 | 0.46496 | 73.1031 | 50.8098 | 4.2722 | 52.99 | 2.8017
2024-01-01 17:00 | 0.46388 | 73.1015 | 50.8446 | 4.3263 | 60.26 | 2.8017
2024-01-01 18:00 | 0.4608 | 73.0893 | 50.9008 | 4.3302 | 60.61 | 2.8017
2024-01-01 19:00 | 0.45509 | 73.0636 | 50.9785 | 4.335 | 60.36 | 2.8017
2024-01-01 20:00 | 0.44624 | 73.0171 | 51.0769 | 4.3548 | 57.4 | 2.8017
2024-01-01 21:00 | 0.4348 | 72.9384 | 51.1908 | 4.414 | 53.86 | 2.8017
2024-01-01 22:00 | 0.42307 | 72.8333 | 51.306 | 4.4211 | 53.45 | 2.8017
2024-01-01 23:00 | 0.41262 | 72.7312 | 51.4068 | 4.4475 | 49.72 | 2.8017
2024-01-02 | 0.40369 | 72.6549 | 51.5016 | 4.4213 | 46.69 | 2.8017
2024-01-02 01:00 | 0.41002 | 72.7139 | 51.387 | 4.4965 | 42.43 | 2.8017
2024-01-02 02:00 | 0.42126 | 72.8026 | 51.2207 | 4.2516 | 41.09 | 2.8017
2024-01-02 03:00 | 0.43821 | 72.9164 | 51.0148 | 4.2667 | 40 | 2.8017
2024-01-02 04:00 | 0.45802 | 73.0303 | 50.8186 | 4.2032 | 37.55 | 2.8017
2024-01-02 05:00 | 0.47795 | 73.1266 | 50.6635 | 4.2401 | 39 | 2.8017
2024-01-02 06:00 | 0.49555 | 73.1903 | 50.5612 | 4.3125 | 42.09 | 2.8017
2024-01-02 07:00 | 0.50905 | 73.2146 | 50.5092 | 4.3254 | 44.96 | 2.8017
2024-01-02 08:00 | 0.51749 | 73.1974 | 50.4944 | 4.2905 | 48.45 | 2.8017
2024-01-02 09:00 | 0.52104 | 73.1486 | 50.5033 | 4.3401 | 52 | 2.8017
2024-01-02 10:00 | 0.52069 | 73.0831 | 50.5262 | 4.5477 | 52 | 2.8017
2024-01-02 11:00 | 0.51795 | 73.0141 | 50.5511 | 4.6233 | 52.15 | 2.8017
2024-01-02 12:00 | 0.51434 | 72.9531 | 50.5712 | 4.6118 | 55.95 | 2.8017
2024-01-02 13:00 | 0.51074 | 72.9056 | 50.582 | 4.6955 | 52 | 2.8017
2024-01-02 14:00 | 0.50767 | 72.8753 | 50.5801 | 4.7843 | 50.69 | 2.8017
2024-01-02 15:00 | 0.50528 | 72.8595 | 50.5677 | 4.6599 | 53.45 | 2.8017
2024-01-02 16:00 | 0.50382 | 72.8583 | 50.5432 | 4.5916 | 59.99 | 2.8017
2024-01-02 17:00 | 0.50167 | 72.8632 | 50.5299 | 4.5165 | 62 | 2.8017
2024-01-02 18:00 | 0.49763 | 72.8684 | 50.5395 | 4.4777 | 63.08 | 2.8017
2024-01-02 19:00 | 0.49058 | 72.8662 | 50.5783 | 4.4666 | 62.17 | 2.8017
2024-01-02 20:00 | 0.47956 | 72.8437 | 50.6479 | 4.3561 | 60.03 | 2.8017
2024-01-02 21:00 | 0.46471 | 72.7825 | 50.7429 | 4.1381 | 55.03 | 2.8017
2024-01-02 22:00 | 0.44873 | 72.6839 | 50.8506 | 3.9376 | 52.25 | 2.8017
2024-01-02 23:00 | 0.43397 | 72.5811 | 50.9414 | 3.9338 | 48.45 | 2.8017
2024-01-03 | 0.42097 | 72.4983 | 51.011 | 4.0077 | 46.11 | 2.8017
2024-01-03 01:00 | 0.42914 | 72.5263 | 50.861 | 3.9135 | 43 | 2.8017
2024-01-03 02:00 | 0.44345 | 72.5888 | 50.655 | 3.7021 | 39.55 | 2.8017
2024-01-03 03:00 | 0.46356 | 72.6856 | 50.4287 | 3.5768 | 35.18 | 2.8017
2024-01-03 04:00 | 0.48632 | 72.7994 | 50.2312 | 3.4491 | 33.45 | 2.8017
2024-01-03 05:00 | 0.50845 | 72.9099 | 50.0924 | 3.2831 | 32.37 | 2.8017
2024-01-03 06:00 | 0.52724 | 73.0019 | 50.0216 | 3.0303 | 31.7 | 2.8017
2024-01-03 07:00 | 0.54123 | 73.0673 | 50.0091 | 2.8322 | 32.63 | 2.8017
2024-01-03 08:00 | 0.54977 | 73.1008 | 50.0377 | 2.8482 | 36.9 | 2.8017
2024-01-03 09:00 | 0.55318 | 73.1049 | 50.0858 | 3.0726 | 36.96 | 2.8017
2024-01-03 10:00 | 0.55229 | 73.0858 | 50.1401 | 3.3867 | 36.96 | 2.8017
2024-01-03 11:00 | 0.54869 | 73.0556 | 50.1929 | 3.8182 | 43.72 | 2.8017
2024-01-03 12:00 | 0.54357 | 73.0195 | 50.2389 | 4.0226 | 47.71 | 2.8017
2024-01-03 13:00 | 0.53805 | 72.9866 | 50.2729 | 4.0513 | 40.41 | 2.8017
2024-01-03 14:00 | 0.53362 | 72.9646 | 50.2872 | 3.9386 | 39.66 | 2.8017
2024-01-03 15:00 | 0.53042 | 72.9561 | 50.2861 | 3.9332 | 39.57 | 2.8017
2024-01-03 16:00 | 0.52741 | 72.9545 | 50.2832 | 3.9043 | 36.11 | 2.8017
2024-01-03 17:00 | 0.5238 | 72.9565 | 50.2845 | 4.0153 | 45.04 | 2.8017
2024-01-03 18:00 | 0.51844 | 72.9571 | 50.3005 | 4.0285 | 52.56 | 2.8017
2024-01-03 19:00 | 0.51052 | 72.952 | 50.3377 | 3.9712 | 45.84 | 2.8017
2024-01-03 20:00 | 0.4992 | 72.9318 | 50.3962 | 3.8742 | 35.83 | 2.8017
2024-01-03 21:00 | 0.48418 | 72.8779 | 50.4747 | 3.8212 | 33.31 | 2.8017
2024-01-03 22:00 | 0.46771 | 72.7858 | 50.5684 | 3.684 | 34.98 | 2.8017
2024-01-03 23:00 | 0.45256 | 72.6855 | 50.6518 | 3.6708 | 27.39 | 2.8017
2024-01-04 | 0.43917 | 72.603 | 50.7211 | 3.581 | 29.33 | 2.8017
2024-01-04 01:00 | 0.44819 | 72.6251 | 50.5547 | 3.4506 | 24.82 | 2.8017
2024-01-04 02:00 | 0.4649 | 72.6721 | 50.3108 | 3.3532 | 24.65 | 2.8017
2024-01-04 03:00 | 0.48795 | 72.7587 | 50.0483 | 3.1007 | 24.8 | 2.8017
2024-01-04 04:00 | 0.51469 | 72.8764 | 49.8155 | 2.8074 | 27.71 | 2.8017
2024-01-04 05:00 | 0.54117 | 73.0016 | 49.6505 | 2.6765 | 28.58 | 2.8017
2024-01-04 06:00 | 0.56308 | 73.1073 | 49.5752 | 2.4461 | 37.04 | 2.8017
2024-01-04 07:00 | 0.57783 | 73.1763 | 49.5793 | 2.2524 | 52.03 | 2.8017
2024-01-04 08:00 | 0.58512 | 73.2062 | 49.6341 | 2.1826 | 55.76 | 2.8017
2024-01-04 09:00 | 0.58618 | 73.2063 | 49.7184 | 2.1461 | 57.06 | 2.8017
2024-01-04 10:00 | 0.58326 | 73.1919 | 49.8088 | 2.2828 | 57.18 | 2.8017
2024-01-04 11:00 | 0.57855 | 73.176 | 49.8884 | 2.4804 | 60 | 2.8017
2024-01-04 12:00 | 0.57383 | 73.1673 | 49.9474 | 2.7064 | 61.27 | 2.8017
2024-01-04 13:00 | 0.56972 | 73.1647 | 49.9857 | 2.89 | 60.28 | 2.8017
2024-01-04 14:00 | 0.56618 | 73.1675 | 50.0095 | 2.9845 | 60.07 | 2.8017
2024-01-04 15:00 | 0.56299 | 73.1732 | 50.0254 | 2.8397 | 59.46 | 2.8017
2024-01-04 16:00 | 0.56053 | 73.1838 | 50.032 | 2.7024 | 61.99 | 2.8017
2024-01-04 17:00 | 0.55773 | 73.1962 | 50.0452 | 2.7078 | 66.82 | 2.8017
2024-01-04 18:00 | 0.55326 | 73.2071 | 50.0813 | 2.6572 | 61.97 | 2.8017
2024-01-04 19:00 | 0.54583 | 73.2108 | 50.1456 | 2.5818 | 55.06 | 2.8017
2024-01-04 20:00 | 0.53449 | 73.1976 | 50.2361 | 2.6273 | 47.34 | 2.8017
2024-01-04 21:00 | 0.51846 | 73.1448 | 50.346 | 2.7463 | 45.64 | 2.8017
2024-01-04 22:00 | 0.50026 | 73.0381 | 50.4575 | 2.842 | 48.93 | 2.8017
2024-01-04 23:00 | 0.48381 | 72.9062 | 50.5376 | 2.9557 | 44.64 | 2.8017
2024-01-05 | 0.47052 | 72.7881 | 50.5829 | 3.0472 | 37.54 | 2.8017
2024-01-05 01:00 | 0.47852 | 72.8437 | 50.4354 | 2.9965 | 40.07 | 2.8017
2024-01-05 02:00 | 0.49387 | 72.9369 | 50.2346 | 2.9136 | 39.81 | 2.8017
2024-01-05 03:00 | 0.51569 | 73.0645 | 50.0151 | 2.8526 | 39.65 | 2.8017
2024-01-05 04:00 | 0.54093 | 73.2031 | 49.8154 | 2.8854 | 40.2 | 2.8017
2024-01-05 05:00 | 0.56555 | 73.3267 | 49.6716 | 2.9726 | 44.26 | 2.8017
2024-01-05 06:00 | 0.58538 | 73.4148 | 49.603 | 3.0134 | 47.06 | 2.8017
2024-01-05 07:00 | 0.59781 | 73.4551 | 49.599 | 3.0304 | 54.96 | 2.8017
2024-01-05 08:00 | 0.60275 | 73.4505 | 49.6358 | 3.0705 | 63.67 | 2.8017
2024-01-05 09:00 | 0.60162 | 73.4124 | 49.6944 | 3.1143 | 64.73 | 2.8017
2024-01-05 10:00 | 0.59669 | 73.3584 | 49.7604 | 3.1861 | 66.07 | 2.8017
2024-01-05 11:00 | 0.59019 | 73.3055 | 49.8237 | 3.3204 | 65.97 | 2.8017
2024-01-05 12:00 | 0.58368 | 73.263 | 49.8798 | 3.5315 | 65.46 | 2.8017
2024-01-05 13:00 | 0.57779 | 73.2337 | 49.9276 | 3.6134 | 63.82 | 2.8017
2024-01-05 14:00 | 0.57316 | 73.2183 | 49.9611 | 3.6442 | 63.87 | 2.8017
2024-01-05 15:00 | 0.56947 | 73.2134 | 49.9833 | 3.5682 | 64.05 | 2.8017
2024-01-05 16:00 | 0.56591 | 73.2151 | 50.0031 | 3.3673 | 64.26 | 2.8017
2024-01-05 17:00 | 0.5618 | 73.2199 | 50.0285 | 3.0729 | 67.14 | 2.8017
2024-01-05 18:00 | 0.55596 | 73.225 | 50.0731 | 2.887 | 61.61 | 2.8017
2024-01-05 19:00 | 0.5467 | 73.2219 | 50.1481 | 2.8681 | 59.16 | 2.8017
2024-01-05 20:00 | 0.53283 | 73.1974 | 50.2522 | 2.9681 | 59.26 | 2.8017
2024-01-05 21:00 | 0.51414 | 73.1286 | 50.3734 | 2.9967 | 53.62 | 2.8017
2024-01-05 22:00 | 0.49372 | 73.0049 | 50.4941 | 2.97 | 53.86 | 2.8017
2024-01-05 23:00 | 0.4758 | 72.8599 | 50.582 | 2.8603 | 47.99 | 2.8017
2024-01-06 | 0.46202 | 72.7322 | 50.6303 | 2.7342 | 44.41 | 2.8017
2024-01-06 01:00 | 0.47103 | 72.7823 | 50.4732 | 2.5938 | 42.94 | 2.8017
2024-01-06 02:00 | 0.4877 | 72.8748 | 50.2554 | 2.4155 | 42.88 | 2.8017
2024-01-06 03:00 | 0.51097 | 73.0077 | 50.0175 | 2.2186 | 42.15 | 2.8017
2024-01-06 04:00 | 0.53759 | 73.1592 | 49.8063 | 2.1429 | 43.23 | 2.8017
2024-01-06 05:00 | 0.56338 | 73.3034 | 49.66 | 2.103 | 44.56 | 2.8017
2024-01-06 06:00 | 0.58429 | 73.4164 | 49.5925 | 2.0392 | 47.4 | 2.8017
2024-01-06 07:00 | 0.59828 | 73.4865 | 49.5871 | 1.7727 | 44.05 | 2.8017
2024-01-06 08:00 | 0.60568 | 73.5177 | 49.6122 | 1.5548 | 53.41 | 2.8017
2024-01-06 09:00 | 0.6077 | 73.5174 | 49.6495 | 1.4475 | 54.8 | 2.8017
2024-01-06 10:00 | 0.60615 | 73.4991 | 49.6882 | 1.4703 | 53.94 | 2.8017
2024-01-06 11:00 | 0.60261 | 73.4742 | 49.7244 | 1.574 | 58.3 | 2.8017
2024-01-06 12:00 | 0.59843 | 73.4519 | 49.755 | 1.6149 | 61.43 | 2.8017
2024-01-06 13:00 | 0.595 | 73.4405 | 49.7736 | 1.5654 | 61.92 | 2.8017
2024-01-06 14:00 | 0.5928 | 73.4424 | 49.7805 | 1.5028 | 57 | 2.8017
2024-01-06 15:00 | 0.59183 | 73.4578 | 49.7781 | 1.4948 | 57.53 | 2.8017
2024-01-06 16:00 | 0.59084 | 73.4795 | 49.7801 | 1.3506 | 61.68 | 2.8017
2024-01-06 17:00 | 0.5891 | 73.5053 | 49.7909 | 1.3486 | 61.84 | 2.8017
2024-01-06 18:00 | 0.58479 | 73.5249 | 49.827 | 1.4017 | 57.46 | 2.8017
2024-01-06 19:00 | 0.57667 | 73.5289 | 49.8938 | 1.4314 | 58.06 | 2.8017
2024-01-06 20:00 | 0.56402 | 73.5066 | 49.9837 | 1.4819 | 59.97 | 2.8017
2024-01-06 21:00 | 0.54694 | 73.4376 | 50.0823 | 1.5659 | 52.95 | 2.8017
2024-01-06 22:00 | 0.52838 | 73.3158 | 50.1763 | 1.5849 | 52.95 | 2.8017
2024-01-06 23:00 | 0.51189 | 73.1737 | 50.2345 | 1.624 | 49.53 | 2.8017
2024-01-07 | 0.49878 | 73.0485 | 50.2598 | 1.6305 | 51.03 | 2.8017
2024-01-07 01:00 | 0.50881 | 73.1129 | 50.1293 | 1.5931 | 50.18 | 2.8017
2024-01-07 02:00 | 0.52615 | 73.2181 | 49.9463 | 1.5904 | 48.97 | 2.8017
2024-01-07 03:00 | 0.54964 | 73.3614 | 49.7501 | 1.6431 | 46.72 | 2.8017
2024-01-07 04:00 | 0.5758 | 73.5189 | 49.5841 | 1.6188 | 46.87 | 2.8017
2024-01-07 05:00 | 0.60073 | 73.6661 | 49.478 | 1.6387 | 50.08 | 2.8017
2024-01-07 06:00 | 0.62056 | 73.7788 | 49.4431 | 1.6961 | 57.34 | 2.8017
2024-01-07 07:00 | 0.63302 | 73.842 | 49.4643 | 1.7424 | 67.8 | 2.8017
2024-01-07 08:00 | 0.63806 | 73.854 | 49.5132 | 1.8067 | 86.51 | 2.8017
2024-01-07 09:00 | 0.63703 | 73.8245 | 49.5709 | 1.9777 | 86.54 | 2.8017
2024-01-07 10:00 | 0.63173 | 73.7687 | 49.6291 | 2.2372 | 85.08 | 2.8017
2024-01-07 11:00 | 0.62392 | 73.7023 | 49.6847 | 2.4736 | 88.74 | 2.8017
2024-01-07 12:00 | 0.61558 | 73.6394 | 49.7314 | 2.5833 | 88.76 | 2.8017
2024-01-07 13:00 | 0.60866 | 73.5907 | 49.7608 | 2.5757 | 84.31 | 2.8017
2024-01-07 14:00 | 0.60359 | 73.5601 | 49.7744 | 2.5864 | 80.4 | 2.8017
2024-01-07 15:00 | 0.59983 | 73.5447 | 49.7797 | 2.5522 | 83.57 | 2.8017
2024-01-07 16:00 | 0.59644 | 73.5394 | 49.7847 | 2.496 | 89.68 | 2.8017
2024-01-07 17:00 | 0.59192 | 73.5365 | 49.8036 | 2.3594 | 100 | 2.8017
2024-01-07 18:00 | 0.58553 | 73.5341 | 49.8409 | 2.3011 | 90.43 | 2.8017
2024-01-07 19:00 | 0.57585 | 73.5241 | 49.9058 | 2.2138 | 80.28 | 2.8017
2024-01-07 20:00 | 0.56181 | 73.4934 | 49.9959 | 2.1244 | 66.8 | 2.8017
2024-01-07 21:00 | 0.54329 | 73.4214 | 50.0997 | 2.0888 | 60.22 | 2.8017
2024-01-07 22:00 | 0.5231 | 73.3012 | 50.2043 | 1.9308 | 59.69 | 2.8017
2024-01-07 23:00 | 0.50538 | 73.166 | 50.2744 | 1.7622 | 52.25 | 2.8017

## Input_MEDIUM
snapshot | heat_demand_mw | temp_supply | temp_return | temp_ambient | electricity_price | cop
2024-01-01 | 0.32121 | 72.0086 | 52.3451 | 5.6688 | 68.7991 | 2.8017
2024-01-01 01:00 | 0.32692 | 71.978 | 52.1666 | 5.6924 | 62.6844 | 2.8017
2024-01-01 02:00 | 0.33995 | 72.0161 | 51.9059 | 5.6289 | 60.2004 | 2.8017
2024-01-01 03:00 | 0.35967 | 72.1259 | 51.6113 | 5.594 | 56.3537 | 2.8017
2024-01-01 04:00 | 0.3828 | 72.2824 | 51.3344 | 5.6361 | 55.4695 | 2.8017
2024-01-01 05:00 | 0.40558 | 72.4531 | 51.1115 | 5.8502 | 54.9571 | 2.8017
2024-01-01 06:00 | 0.42447 | 72.6052 | 50.9602 | 5.912 | 53.5324 | 2.8017
2024-01-01 07:00 | 0.43748 | 72.7185 | 50.8769 | 5.8771 | 60.9146 | 2.8017
2024-01-01 08:00 | 0.44452 | 72.7895 | 50.8453 | 5.9945 | 64.9195 | 2.8017
2024-01-01 09:00 | 0.446 | 72.8216 | 50.8563 | 5.9885 | 64.6992 | 2.8017
2024-01-01 10:00 | 0.44402 | 72.8312 | 50.8933 | 6.2017 | 60.8954 | 2.8017
2024-01-01 11:00 | 0.44057 | 72.8305 | 50.944 | 6.335 | 60.344 | 2.8017
2024-01-01 12:00 | 0.43732 | 72.8295 | 50.9946 | 6.4042 | 57.8528 | 2.8017
2024-01-01 13:00 | 0.43531 | 72.8336 | 51.0306 | 6.6514 | 55.4409 | 2.8017
2024-01-01 14:00 | 0.43384 | 72.8374 | 51.0633 | 6.7567 | 59.8816 | 2.8017
2024-01-01 15:00 | 0.43246 | 72.8379 | 51.0971 | 6.2671 | 66.6941 | 2.8017
2024-01-01 16:00 | 0.43168 | 72.8406 | 51.1249 | 5.9637 | 76.5461 | 2.8017
2024-01-01 17:00 | 0.43042 | 72.842 | 51.1584 | 5.8662 | 88.4034 | 2.8017
2024-01-01 18:00 | 0.42671 | 72.8336 | 51.2211 | 5.7121 | 91.3571 | 2.8017
2024-01-01 19:00 | 0.41985 | 72.8112 | 51.3153 | 5.5233 | 87.1599 | 2.8017
2024-01-01 20:00 | 0.40972 | 72.7688 | 51.4324 | 5.5097 | 79.5799 | 2.8017
2024-01-01 21:00 | 0.39681 | 72.6894 | 51.5668 | 5.5051 | 73.3514 | 2.8017
2024-01-01 22:00 | 0.38413 | 72.5788 | 51.7028 | 5.4633 | 71.4214 | 2.8017
2024-01-01 23:00 | 0.37365 | 72.4687 | 51.8136 | 5.4113 | 63.5831 | 2.8017
2024-01-02 | 0.36525 | 72.3841 | 51.9055 | 5.3219 | 78.564 | 2.8017
2024-01-02 01:00 | 0.37239 | 72.4517 | 51.7381 | 5.3477 | 73.7752 | 2.8017
2024-01-02 02:00 | 0.3863 | 72.5336 | 51.4894 | 5.3478 | 71.1156 | 2.8017
2024-01-02 03:00 | 0.40672 | 72.6295 | 51.186 | 5.1906 | 68.0837 | 2.8017
2024-01-02 04:00 | 0.43064 | 72.7274 | 50.8898 | 5.0736 | 67.7188 | 2.8017
2024-01-02 05:00 | 0.45413 | 72.8105 | 50.6513 | 5.1144 | 69.6363 | 2.8017
2024-01-02 06:00 | 0.47396 | 72.8643 | 50.4924 | 5.1436 | 77.3715 | 2.8017
2024-01-02 07:00 | 0.4876 | 72.8795 | 50.4158 | 5.2541 | 92.7204 | 2.8017
2024-01-02 08:00 | 0.49454 | 72.8582 | 50.4038 | 5.171 | 106.1665 | 2.8017
2024-01-02 09:00 | 0.49627 | 72.8176 | 50.428 | 5.3247 | 97.493 | 2.8017
2024-01-02 10:00 | 0.49456 | 72.7699 | 50.4673 | 5.6629 | 86.3332 | 2.8017
2024-01-02 11:00 | 0.49108 | 72.7238 | 50.5128 | 6.1283 | 79.8596 | 2.8017
2024-01-02 12:00 | 0.48698 | 72.6836 | 50.5565 | 6.2822 | 74.8658 | 2.8017
2024-01-02 13:00 | 0.48302 | 72.6522 | 50.5947 | 6.2103 | 73.5743 | 2.8017
2024-01-02 14:00 | 0.48149 | 72.6392 | 50.6016 | 5.9493 | 79.5221 | 2.8017
2024-01-02 15:00 | 0.48191 | 72.6423 | 50.5818 | 5.9641 | 90.9303 | 2.8017
2024-01-02 16:00 | 0.48219 | 72.6506 | 50.5624 | 5.7909 | 104.1423 | 2.8017
2024-01-02 17:00 | 0.48185 | 72.6622 | 50.5495 | 5.7105 | 117.4899 | 2.8017
2024-01-02 18:00 | 0.47954 | 72.6724 | 50.558 | 5.5944 | 121.3437 | 2.8017
2024-01-02 19:00 | 0.47387 | 72.6736 | 50.6027 | 5.6602 | 115.3367 | 2.8017
2024-01-02 20:00 | 0.46357 | 72.652 | 50.6885 | 5.5721 | 99.2993 | 2.8017
2024-01-02 21:00 | 0.44899 | 72.5933 | 50.8052 | 5.452 | 91.2112 | 2.8017
2024-01-02 22:00 | 0.43256 | 72.4933 | 50.9392 | 5.509 | 86.67 | 2.8017
2024-01-02 23:00 | 0.41718 | 72.3775 | 51.0561 | 5.4341 | 77.5908 | 2.8017
2024-01-03 | 0.4039 | 72.2778 | 51.1476 | 5.3965 | 75.0452 | 2.8017
2024-01-03 01:00 | 0.4113 | 72.2934 | 51.0231 | 5.3515 | 70.2589 | 2.8017
2024-01-03 02:00 | 0.42412 | 72.3571 | 50.8503 | 5.3674 | 68.2031 | 2.8017
2024-01-03 03:00 | 0.44204 | 72.4617 | 50.6559 | 5.1521 | 64.9565 | 2.8017
2024-01-03 04:00 | 0.46283 | 72.5884 | 50.475 | 5.015 | 63.9718 | 2.8017
2024-01-03 05:00 | 0.48312 | 72.7119 | 50.3424 | 5.0137 | 64.2554 | 2.8017
2024-01-03 06:00 | 0.5004 | 72.8131 | 50.266 | 5.2654 | 66.2302 | 2.8017
2024-01-03 07:00 | 0.51217 | 72.8753 | 50.248 | 5.4858 | 77.5676 | 2.8017
2024-01-03 08:00 | 0.51784 | 72.8961 | 50.2758 | 5.495 | 85.7614 | 2.8017
2024-01-03 09:00 | 0.51812 | 72.8819 | 50.3304 | 6.0228 | 84.0552 | 2.8017
2024-01-03 10:00 | 0.51416 | 72.8434 | 50.4049 | 6.4222 | 79.2401 | 2.8017
2024-01-03 11:00 | 0.50788 | 72.7947 | 50.4858 | 6.6412 | 76.7767 | 2.8017
2024-01-03 12:00 | 0.50084 | 72.7481 | 50.5635 | 6.8544 | 73.843 | 2.8017
2024-01-03 13:00 | 0.49393 | 72.7087 | 50.6313 | 7.0657 | 71.9152 | 2.8017
2024-01-03 14:00 | 0.48756 | 72.6776 | 50.686 | 7.0808 | 75.5381 | 2.8017
2024-01-03 15:00 | 0.48132 | 72.6534 | 50.7325 | 6.762 | 83.0527 | 2.8017
2024-01-03 16:00 | 0.47623 | 72.6377 | 50.7573 | 6.4795 | 92.873 | 2.8017
2024-01-03 17:00 | 0.47148 | 72.6285 | 50.7739 | 6.3697 | 103.7354 | 2.8017
2024-01-03 18:00 | 0.46518 | 72.6189 | 50.8053 | 6.3002 | 107.241 | 2.8017
2024-01-03 19:00 | 0.45606 | 72.6034 | 50.8675 | 6.1642 | 102.2051 | 2.8017
2024-01-03 20:00 | 0.44339 | 72.5754 | 50.9628 | 6.1313 | 92.5188 | 2.8017
2024-01-03 21:00 | 0.42632 | 72.5147 | 51.1003 | 6.3702 | 84.9725 | 2.8017
2024-01-03 22:00 | 0.40684 | 72.4132 | 51.2758 | 6.4247 | 80.9922 | 2.8017
2024-01-03 23:00 | 0.38884 | 72.304 | 51.4464 | 6.3997 | 72.0982 | 2.8017
2024-01-04 | 0.37307 | 72.2158 | 51.6011 | 6.2374 | 70.6332 | 2.8017
2024-01-04 01:00 | 0.37922 | 72.2222 | 51.4698 | 6.1531 | 64.5142 | 2.8017
2024-01-04 02:00 | 0.39148 | 72.2618 | 51.2729 | 6.0743 | 62.0232 | 2.8017
2024-01-04 03:00 | 0.40961 | 72.3363 | 51.0404 | 6.0328 | 58.172 | 2.8017
2024-01-04 04:00 | 0.43031 | 72.4263 | 50.8269 | 5.9428 | 57.3079 | 2.8017
2024-01-04 05:00 | 0.45015 | 72.5135 | 50.6666 | 5.9714 | 56.7028 | 2.8017
2024-01-04 06:00 | 0.46675 | 72.5807 | 50.5674 | 6.0139 | 54.3837 | 2.8017
2024-01-04 07:00 | 0.47818 | 72.6189 | 50.5291 | 5.9062 | 61.7787 | 2.8017
2024-01-04 08:00 | 0.4844 | 72.6289 | 50.5332 | 5.7614 | 65.8534 | 2.8017
2024-01-04 09:00 | 0.48592 | 72.6178 | 50.5663 | 5.6758 | 65.6572 | 2.8017
2024-01-04 10:00 | 0.48523 | 72.6007 | 50.6039 | 5.9134 | 61.8246 | 2.8017
2024-01-04 11:00 | 0.48243 | 72.5804 | 50.6483 | 6.3398 | 61.2801 | 2.8017
2024-01-04 12:00 | 0.47797 | 72.5576 | 50.698 | 6.714 | 58.6641 | 2.8017
2024-01-04 13:00 | 0.47294 | 72.536 | 50.7463 | 6.7975 | 56.2052 | 2.8017
2024-01-04 14:00 | 0.46852 | 72.5223 | 50.7816 | 6.5517 | 60.6597 | 2.8017
2024-01-04 15:00 | 0.46528 | 72.5181 | 50.7971 | 6.1939 | 67.3378 | 2.8017
2024-01-04 16:00 | 0.46278 | 72.5223 | 50.8008 | 5.8384 | 77.3115 | 2.8017
2024-01-04 17:00 | 0.46033 | 72.5323 | 50.8024 | 5.5291 | 89.3361 | 2.8017
2024-01-04 18:00 | 0.45676 | 72.5444 | 50.8195 | 5.4101 | 92.4683 | 2.8017
2024-01-04 19:00 | 0.45028 | 72.5504 | 50.8657 | 5.3205 | 88.1474 | 2.8017
2024-01-04 20:00 | 0.43963 | 72.5379 | 50.9479 | 5.2721 | 80.4239 | 2.8017
2024-01-04 21:00 | 0.42494 | 72.4912 | 51.0589 | 5.3204 | 74.127 | 2.8017
2024-01-04 22:00 | 0.40878 | 72.407 | 51.1908 | 5.4576 | 72.0598 | 2.8017
2024-01-04 23:00 | 0.39364 | 72.3109 | 51.3154 | 5.4932 | 64.1771 | 2.8017
2024-01-05 | 0.38019 | 72.2329 | 51.4235 | 5.6211 | 73.2737 | 2.8017
2024-01-05 01:00 | 0.3885 | 72.2191 | 51.2384 | 5.5444 | 69.818 | 2.8017
2024-01-05 02:00 | 0.40406 | 72.2233 | 50.9637 | 5.4188 | 67.4332 | 2.8017
2024-01-05 03:00 | 0.42608 | 72.2715 | 50.6537 | 5.2221 | 63.4706 | 2.8017
2024-01-05 04:00 | 0.45118 | 72.3551 | 50.3737 | 5.1483 | 64.8361 | 2.8017
2024-01-05 05:00 | 0.4756 | 72.4501 | 50.1641 | 5.0938 | 74.6507 | 2.8017
2024-01-05 06:00 | 0.49589 | 72.5381 | 50.0368 | 4.8541 | 101.6298 | 2.8017
2024-01-05 07:00 | 0.50991 | 72.6019 | 49.9875 | 4.9274 | 131.6329 | 2.8017
2024-01-05 08:00 | 0.51695 | 72.6343 | 49.9996 | 4.9336 | 157.009 | 2.8017
2024-01-05 09:00 | 0.51801 | 72.6412 | 50.0543 | 5.2388 | 130.249 | 2.8017
2024-01-05 10:00 | 0.51421 | 72.6294 | 50.1424 | 5.4963 | 105.2677 | 2.8017
2024-01-05 11:00 | 0.50827 | 72.6117 | 50.2454 | 5.5874 | 91.1246 | 2.8017
2024-01-05 12:00 | 0.50267 | 72.6021 | 50.3324 | 5.749 | 83.4055 | 2.8017
2024-01-05 13:00 | 0.4989 | 72.6027 | 50.3893 | 5.9962 | 85.8592 | 2.8017
2024-01-05 14:00 | 0.49618 | 72.6085 | 50.4265 | 6.059 | 97.6 | 2.8017
2024-01-05 15:00 | 0.49402 | 72.616 | 50.4492 | 5.8747 | 119.1315 | 2.8017
2024-01-05 16:00 | 0.49209 | 72.625 | 50.4613 | 5.6374 | 144.624 | 2.8017
2024-01-05 17:00 | 0.48895 | 72.6324 | 50.4841 | 5.2718 | 171.4683 | 2.8017
2024-01-05 18:00 | 0.48429 | 72.6377 | 50.5191 | 5.0382 | 170.022 | 2.8017
2024-01-05 19:00 | 0.47739 | 72.6403 | 50.5795 | 4.9482 | 154.8672 | 2.8017
2024-01-05 20:00 | 0.46641 | 72.629 | 50.6798 | 4.706 | 111.3572 | 2.8017
2024-01-05 21:00 | 0.45112 | 72.5825 | 50.8107 | 4.6733 | 98.6806 | 2.8017
2024-01-05 22:00 | 0.43359 | 72.4841 | 50.9568 | 4.8828 | 90.9188 | 2.8017
2024-01-05 23:00 | 0.41771 | 72.362 | 51.0791 | 4.8049 | 81.2917 | 2.8017
2024-01-06 | 0.40503 | 72.2581 | 51.1662 | 4.5457 | 84.6965 | 2.8017
2024-01-06 01:00 | 0.4143 | 72.3124 | 50.9957 | 4.5997 | 80.405 | 2.8017
2024-01-06 02:00 | 0.43084 | 72.4014 | 50.7533 | 4.4345 | 77.1304 | 2.8017
2024-01-06 03:00 | 0.45396 | 72.5295 | 50.4774 | 4.1197 | 74.5295 | 2.8017
2024-01-06 04:00 | 0.48016 | 72.6764 | 50.2279 | 4.0975 | 75.2005 | 2.8017
2024-01-06 05:00 | 0.50516 | 72.8125 | 50.0479 | 4.1465 | 80.2448 | 2.8017
2024-01-06 06:00 | 0.52516 | 72.9132 | 49.9508 | 4.1487 | 100.4182 | 2.8017
2024-01-06 07:00 | 0.53768 | 72.9648 | 49.9262 | 4.1612 | 131.5403 | 2.8017
2024-01-06 08:00 | 0.54297 | 72.9737 | 49.9512 | 4.156 | 156.7423 | 2.8017
2024-01-06 09:00 | 0.54233 | 72.9517 | 50.0085 | 4.1809 | 129.8734 | 2.8017
2024-01-06 10:00 | 0.53855 | 72.9191 | 50.0763 | 4.6725 | 104.5617 | 2.8017
2024-01-06 11:00 | 0.5325 | 72.8831 | 50.1549 | 5.0353 | 90.3119 | 2.8017
2024-01-06 12:00 | 0.52587 | 72.8512 | 50.2308 | 5.1674 | 82.5008 | 2.8017
2024-01-06 13:00 | 0.52043 | 72.8304 | 50.2873 | 5.3597 | 84.9825 | 2.8017
2024-01-06 14:00 | 0.5169 | 72.8207 | 50.3189 | 5.5108 | 96.7378 | 2.8017
2024-01-06 15:00 | 0.51497 | 72.8194 | 50.3304 | 5.332 | 118.5294 | 2.8017
2024-01-06 16:00 | 0.51383 | 72.8239 | 50.3316 | 5.2672 | 144.3045 | 2.8017
2024-01-06 17:00 | 0.51202 | 72.8284 | 50.3384 | 5.0755 | 171.4315 | 2.8017
2024-01-06 18:00 | 0.50801 | 72.8302 | 50.3695 | 5.0888 | 170.0681 | 2.8017
2024-01-06 19:00 | 0.50013 | 72.8235 | 50.4401 | 5.0599 | 154.9092 | 2.8017
2024-01-06 20:00 | 0.48765 | 72.8002 | 50.549 | 5.1432 | 121.352 | 2.8017
2024-01-06 21:00 | 0.46991 | 72.7363 | 50.6966 | 4.9782 | 107.537 | 2.8017
2024-01-06 22:00 | 0.45034 | 72.6241 | 50.8504 | 4.8773 | 99.0782 | 2.8017
2024-01-06 23:00 | 0.43292 | 72.4916 | 50.972 | 4.7141 | 88.5867 | 2.8017
2024-01-07 | 0.41887 | 72.3766 | 51.0616 | 4.4353 | 85.1118 | 2.8017
2024-01-07 01:00 | 0.42759 | 72.4254 | 50.8895 | 4.4454 | 80.7992 | 2.8017
2024-01-07 02:00 | 0.44392 | 72.514 | 50.6478 | 4.5148 | 77.5085 | 2.8017
2024-01-07 03:00 | 0.46653 | 72.6383 | 50.3793 | 4.4614 | 74.8948 | 2.8017
2024-01-07 04:00 | 0.49184 | 72.7748 | 50.14 | 4.6708 | 75.5692 | 2.8017
2024-01-07 05:00 | 0.51576 | 72.8981 | 49.9683 | 4.9016 | 80.6382 | 2.8017
2024-01-07 06:00 | 0.53397 | 72.9821 | 49.8849 | 5.0084 | 100.9106 | 2.8017
2024-01-07 07:00 | 0.5447 | 73.0181 | 49.8729 | 5.2741 | 132.1855 | 2.8017
2024-01-07 08:00 | 0.54738 | 73.0065 | 49.916 | 5.2693 | 156.754 | 2.8017
2024-01-07 09:00 | 0.54435 | 72.9632 | 49.982 | 5.506 | 129.8831 | 2.8017
2024-01-07 10:00 | 0.53685 | 72.8991 | 50.0732 | 5.9485 | 104.5696 | 2.8017
2024-01-07 11:00 | 0.52708 | 72.8338 | 50.1802 | 6.3151 | 90.3187 | 2.8017
2024-01-07 12:00 | 0.51703 | 72.7776 | 50.2871 | 6.4752 | 82.507 | 2.8017
2024-01-07 13:00 | 0.5089 | 72.7376 | 50.369 | 6.7447 | 84.9889 | 2.8017
2024-01-07 14:00 | 0.50274 | 72.71 | 50.4298 | 6.8639 | 96.7451 | 2.8017
2024-01-07 15:00 | 0.49763 | 72.6934 | 50.4798 | 6.6009 | 118.5383 | 2.8017
2024-01-07 16:00 | 0.49359 | 72.6841 | 50.5097 | 6.4517 | 144.3153 | 2.8017
2024-01-07 17:00 | 0.4897 | 72.6785 | 50.5327 | 6.3762 | 171.4443 | 2.8017
2024-01-07 18:00 | 0.48388 | 72.6689 | 50.5749 | 6.2467 | 170.0808 | 2.8017
2024-01-07 19:00 | 0.47509 | 72.6527 | 50.6508 | 6.1661 | 154.9208 | 2.8017
2024-01-07 20:00 | 0.46207 | 72.6211 | 50.7686 | 6.1553 | 121.9471 | 2.8017
2024-01-07 21:00 | 0.44434 | 72.5556 | 50.9266 | 6.2083 | 108.0644 | 2.8017
2024-01-07 22:00 | 0.42433 | 72.4451 | 51.106 | 6.209 | 99.564 | 2.8017
2024-01-07 23:00 | 0.40588 | 72.3168 | 51.2638 | 6.0898 | 89.0211 | 2.8017

## Input_WARM
snapshot | heat_demand_mw | temp_supply | temp_return | temp_ambient | electricity_price | cop
2024-01-01 | 0.32121 | 72.0086 | 52.3451 | 7.1912 | 0.1 | 2.8017
2024-01-01 01:00 | 0.32536 | 71.9759 | 52.1925 | 7.0014 | 0.01 | 2.8017
2024-01-01 02:00 | 0.3361 | 72.0012 | 51.9537 | 6.8409 | 0 | 2.8017
2024-01-01 03:00 | 0.35339 | 72.0951 | 51.671 | 6.9192 | -0.01 | 2.8017
2024-01-01 04:00 | 0.37436 | 72.2349 | 51.3956 | 6.997 | -0.03 | 2.8017
2024-01-01 05:00 | 0.39538 | 72.3893 | 51.1665 | 7.1413 | -0.02 | 2.8017
2024-01-01 06:00 | 0.41317 | 72.5289 | 51.0034 | 7.2482 | -0.05 | 2.8017
2024-01-01 07:00 | 0.42576 | 72.6345 | 50.9062 | 7.3111 | -0.02 | 2.8017
2024-01-01 08:00 | 0.43278 | 72.7014 | 50.8626 | 7.34 | 0 | 2.8017
2024-01-01 09:00 | 0.43473 | 72.7341 | 50.8634 | 7.5246 | 0.04 | 2.8017
2024-01-01 10:00 | 0.43296 | 72.7434 | 50.8988 | 7.7184 | 0.06 | 2.8017
2024-01-01 11:00 | 0.429 | 72.7399 | 50.9571 | 7.7119 | 0.54 | 2.8017
2024-01-01 12:00 | 0.42507 | 72.7345 | 51.0134 | 7.5926 | 2.24 | 2.8017
2024-01-01 13:00 | 0.42312 | 72.7352 | 51.0449 | 7.6311 | 1.96 | 2.8017
2024-01-01 14:00 | 0.42225 | 72.7374 | 51.0674 | 7.8368 | 1.04 | 2.8017
2024-01-01 15:00 | 0.42101 | 72.7343 | 51.0992 | 7.7531 | 3.66 | 2.8017
2024-01-01 16:00 | 0.41925 | 72.726 | 51.1397 | 7.4709 | 43.06 | 2.8017
2024-01-01 17:00 | 0.41649 | 72.7109 | 51.1929 | 7.4203 | 49.93 | 2.8017
2024-01-01 18:00 | 0.41148 | 72.6862 | 51.2756 | 7.252 | 58 | 2.8017
2024-01-01 19:00 | 0.40367 | 72.6518 | 51.3907 | 7.0809 | 54.25 | 2.8017
2024-01-01 20:00 | 0.39248 | 72.6028 | 51.538 | 6.9577 | 48.01 | 2.8017
2024-01-01 21:00 | 0.378 | 72.5178 | 51.7092 | 6.9161 | 42.95 | 2.8017
2024-01-01 22:00 | 0.36341 | 72.3928 | 51.8866 | 6.8811 | 47.09 | 2.8017
2024-01-01 23:00 | 0.35158 | 72.265 | 52.0277 | 6.7618 | 35.55 | 2.8017
2024-01-02 | 0.34235 | 72.1662 | 52.1383 | 6.5785 | 30.59 | 2.8017
2024-01-02 01:00 | 0.34818 | 72.2317 | 51.9897 | 6.3313 | 20.07 | 2.8017
2024-01-02 02:00 | 0.36049 | 72.301 | 51.7549 | 5.8056 | 31.03 | 2.8017
2024-01-02 03:00 | 0.38023 | 72.3847 | 51.4425 | 5.3973 | 18.39 | 2.8017
2024-01-02 04:00 | 0.40484 | 72.4784 | 51.117 | 5.2723 | 11.08 | 2.8017
2024-01-02 05:00 | 0.42958 | 72.562 | 50.8511 | 5.1634 | 13.78 | 2.8017
2024-01-02 06:00 | 0.45054 | 72.6207 | 50.6711 | 5.1952 | 47.63 | 2.8017
2024-01-02 07:00 | 0.46498 | 72.6441 | 50.5805 | 5.2421 | 58.1 | 2.8017
2024-01-02 08:00 | 0.47239 | 72.6349 | 50.5638 | 5.3518 | 65.67 | 2.8017
2024-01-02 09:00 | 0.4736 | 72.6033 | 50.5995 | 5.5249 | 64.73 | 2.8017
2024-01-02 10:00 | 0.47073 | 72.5619 | 50.6612 | 5.7622 | 68.98 | 2.8017
2024-01-02 11:00 | 0.46587 | 72.5198 | 50.7309 | 5.963 | 73.54 | 2.8017
2024-01-02 12:00 | 0.46113 | 72.4842 | 50.7897 | 5.9707 | 78.16 | 2.8017
2024-01-02 13:00 | 0.45784 | 72.4614 | 50.8265 | 6.0076 | 78.87 | 2.8017
2024-01-02 14:00 | 0.45663 | 72.4526 | 50.8336 | 5.9737 | 79.24 | 2.8017
2024-01-02 15:00 | 0.45737 | 72.4566 | 50.8154 | 5.8788 | 79.96 | 2.8017
2024-01-02 16:00 | 0.45904 | 72.4694 | 50.7856 | 5.8029 | 83.46 | 2.8017
2024-01-02 17:00 | 0.46031 | 72.4862 | 50.7598 | 5.8104 | 80.92 | 2.8017
2024-01-02 18:00 | 0.45985 | 72.5013 | 50.754 | 5.9012 | 74.95 | 2.8017
2024-01-02 19:00 | 0.45571 | 72.5056 | 50.7898 | 5.924 | 63.18 | 2.8017
2024-01-02 20:00 | 0.44688 | 72.4889 | 50.8714 | 5.9979 | 57.11 | 2.8017
2024-01-02 21:00 | 0.43335 | 72.4351 | 50.995 | 6.0843 | 46.89 | 2.8017
2024-01-02 22:00 | 0.41791 | 72.3387 | 51.1399 | 6.202 | 40 | 2.8017
2024-01-02 23:00 | 0.40372 | 72.2293 | 51.2683 | 6.4312 | 7.43 | 2.8017
2024-01-03 | 0.39131 | 72.14 | 51.382 | 6.7011 | -0.08 | 2.8017
2024-01-03 01:00 | 0.39952 | 72.1672 | 51.2176 | 6.9772 | -1.23 | 2.8017
2024-01-03 02:00 | 0.41394 | 72.2279 | 50.9921 | 7.3683 | -1.3 | 2.8017
2024-01-03 03:00 | 0.43331 | 72.3204 | 50.7463 | 7.8276 | -1.31 | 2.8017
2024-01-03 04:00 | 0.45412 | 72.4227 | 50.5345 | 8.2498 | -1.31 | 2.8017
2024-01-03 05:00 | 0.4718 | 72.5051 | 50.4017 | 8.1945 | -1.38 | 2.8017
2024-01-03 06:00 | 0.4844 | 72.5545 | 50.3403 | 8.1812 | 1.09 | 2.8017
2024-01-03 07:00 | 0.49096 | 72.5669 | 50.3401 | 8.1049 | 40.59 | 2.8017
2024-01-03 08:00 | 0.49194 | 72.5514 | 50.3845 | 8.105 | 59.61 | 2.8017
2024-01-03 09:00 | 0.4884 | 72.5208 | 50.463 | 8.234 | 60.61 | 2.8017
2024-01-03 10:00 | 0.48189 | 72.486 | 50.5658 | 8.3646 | 57 | 2.8017
2024-01-03 11:00 | 0.47481 | 72.4573 | 50.6671 | 8.5884 | 54.89 | 2.8017
2024-01-03 12:00 | 0.46805 | 72.4362 | 50.7607 | 8.7674 | 53.89 | 2.8017
2024-01-03 13:00 | 0.46158 | 72.4206 | 50.8452 | 8.884 | 54.42 | 2.8017
2024-01-03 14:00 | 0.45494 | 72.4067 | 50.9288 | 8.6881 | 60.86 | 2.8017
2024-01-03 15:00 | 0.44889 | 72.396 | 50.999 | 8.4049 | 67.18 | 2.8017
2024-01-03 16:00 | 0.44332 | 72.3872 | 51.0579 | 8.0503 | 73.59 | 2.8017
2024-01-03 17:00 | 0.43743 | 72.3785 | 51.1186 | 7.6445 | 82.28 | 2.8017
2024-01-03 18:00 | 0.43068 | 72.3715 | 51.1891 | 7.4752 | 82.97 | 2.8017
2024-01-03 19:00 | 0.42143 | 72.3616 | 51.2924 | 7.2222 | 79.03 | 2.8017
2024-01-03 20:00 | 0.40837 | 72.341 | 51.441 | 6.986 | 73.23 | 2.8017
2024-01-03 21:00 | 0.39068 | 72.2872 | 51.6313 | 6.8091 | 67.41 | 2.8017
2024-01-03 22:00 | 0.37094 | 72.1875 | 51.8433 | 6.4901 | 65 | 2.8017
2024-01-03 23:00 | 0.35388 | 72.0768 | 52.0293 | 6.1343 | 58.12 | 2.8017
2024-01-04 | 0.34095 | 71.9944 | 52.1675 | 5.7849 | 57.3 | 2.8017
2024-01-04 01:00 | 0.35021 | 71.9838 | 51.9394 | 5.2473 | 50.46 | 2.8017
2024-01-04 02:00 | 0.36708 | 72.0237 | 51.6195 | 4.643 | 40 | 2.8017
2024-01-04 03:00 | 0.39176 | 72.1269 | 51.2427 | 4.1751 | 25.48 | 2.8017
2024-01-04 04:00 | 0.42082 | 72.2765 | 50.8902 | 3.6782 | 35 | 2.8017
2024-01-04 05:00 | 0.44951 | 72.4424 | 50.6223 | 3.0663 | 57.73 | 2.8017
2024-01-04 06:00 | 0.47402 | 72.5935 | 50.4521 | 2.4641 | 72.65 | 2.8017
2024-01-04 07:00 | 0.49222 | 72.7111 | 50.3647 | 1.7151 | 85.02 | 2.8017
2024-01-04 08:00 | 0.50436 | 72.7969 | 50.325 | 1.1536 | 91.47 | 2.8016
2024-01-04 09:00 | 0.51193 | 72.8587 | 50.3048 | 0.95819 | 94.2 | 2.8016
2024-01-04 10:00 | 0.51654 | 72.9033 | 50.2881 | 0.8429 | 91.61 | 2.8016
2024-01-04 11:00 | 0.51996 | 72.939 | 50.2634 | 0.80507 | 90.03 | 2.8016
2024-01-04 12:00 | 0.52379 | 72.9757 | 50.2228 | 0.84962 | 86.3 | 2.8016
2024-01-04 13:00 | 0.52857 | 73.0179 | 50.169 | 0.88794 | 85.96 | 2.8016
2024-01-04 14:00 | 0.53459 | 73.0684 | 50.1065 | 1.0248 | 92.11 | 2.8016
2024-01-04 15:00 | 0.54103 | 73.1248 | 50.0497 | 1.0094 | 98.62 | 2.8016
2024-01-04 16:00 | 0.54759 | 73.1875 | 50.0027 | 0.97826 | 105.73 | 2.8016
2024-01-04 17:00 | 0.55297 | 73.2521 | 49.9775 | 0.98064 | 133.23 | 2.8016
2024-01-04 18:00 | 0.55576 | 73.3107 | 49.983 | 0.88958 | 144.65 | 2.8016
2024-01-04 19:00 | 0.55478 | 73.3566 | 50.0209 | 0.7785 | 125 | 2.8016
2024-01-04 20:00 | 0.5492 | 73.3752 | 50.0818 | 0.6473 | 103.59 | 2.8016
2024-01-04 21:00 | 0.53923 | 73.3471 | 50.1543 | 0.53874 | 100.01 | 2.8016
2024-01-04 22:00 | 0.52735 | 73.269 | 50.2228 | 0.45826 | 94.86 | 2.8016
2024-01-04 23:00 | 0.51629 | 73.1683 | 50.2614 | 0.52815 | 88.83 | 2.8016
2024-01-05 | 0.50755 | 73.0836 | 50.2726 | 0.53674 | 86.08 | 2.8016
2024-01-05 01:00 | 0.52219 | 73.1991 | 50.0992 | 0.46673 | 80.51 | 2.8016
2024-01-05 02:00 | 0.54319 | 73.3511 | 49.8906 | 0.55655 | 77.01 | 2.8016
2024-01-05 03:00 | 0.56901 | 73.5352 | 49.699 | 0.73118 | 73.21 | 2.8016
2024-01-05 04:00 | 0.59618 | 73.728 | 49.562 | 0.84702 | 74.05 | 2.8016
2024-01-05 05:00 | 0.62055 | 73.8978 | 49.5015 | 0.91399 | 76.03 | 2.8016
2024-01-05 06:00 | 0.63887 | 74.0191 | 49.5111 | 0.95542 | 81 | 2.8016
2024-01-05 07:00 | 0.64971 | 74.0801 | 49.5625 | 1.0323 | 87 | 2.8016
2024-01-05 08:00 | 0.65346 | 74.0804 | 49.6217 | 0.99209 | 89.57 | 2.8016
2024-01-05 09:00 | 0.65266 | 74.039 | 49.6662 | 0.90472 | 94.93 | 2.8016
2024-01-05 10:00 | 0.64944 | 73.9794 | 49.6943 | 0.90254 | 96.28 | 2.8016
2024-01-05 11:00 | 0.6452 | 73.919 | 49.7095 | 0.95622 | 98.22 | 2.8016
2024-01-05 12:00 | 0.6409 | 73.8699 | 49.7174 | 1.0439 | 92.24 | 2.8016
2024-01-05 13:00 | 0.63722 | 73.8392 | 49.7197 | 1.0723 | 91.54 | 2.8016
2024-01-05 14:00 | 0.63415 | 73.8263 | 49.7185 | 1.0852 | 96.41 | 2.8016
2024-01-05 15:00 | 0.63161 | 73.8288 | 49.7169 | 1.0279 | 100.05 | 2.8016
2024-01-05 16:00 | 0.62896 | 73.8412 | 49.7211 | 0.93253 | 102.97 | 2.8016
2024-01-05 17:00 | 0.62499 | 73.8566 | 49.7433 | 0.86237 | 107.38 | 2.8016
2024-01-05 18:00 | 0.61869 | 73.8699 | 49.7907 | 0.67833 | 108.45 | 2.8016
2024-01-05 19:00 | 0.60926 | 73.8739 | 49.8625 | 0.46793 | 103.96 | 2.8016
2024-01-05 20:00 | 0.59596 | 73.8559 | 49.9521 | 0.39659 | 100.09 | 2.8016
2024-01-05 21:00 | 0.57836 | 73.7918 | 50.0447 | 0.44411 | 94.19 | 2.8016
2024-01-05 22:00 | 0.55899 | 73.6735 | 50.1263 | 0.50467 | 94.92 | 2.8016
2024-01-05 23:00 | 0.54152 | 73.5304 | 50.1717 | 0.56776 | 86.8 | 2.8016
2024-01-06 | 0.52809 | 73.39 | 50.1667 | 0.63645 | 82.25 | 2.8016
2024-01-06 01:00 | 0.53475 | 73.4314 | 50.0969 | 0.69915 | 80.2 | 2.8016
2024-01-06 02:00 | 0.54732 | 73.5183 | 49.9955 | 0.75739 | 76.13 | 2.8016
2024-01-06 03:00 | 0.56503 | 73.6408 | 49.8902 | 0.83462 | 73.01 | 2.8016
2024-01-06 04:00 | 0.58519 | 73.775 | 49.8085 | 0.79687 | 73.01 | 2.8016
2024-01-06 05:00 | 0.60482 | 73.8992 | 49.7674 | 0.77957 | 74.59 | 2.8016
2024-01-06 06:00 | 0.6212 | 73.9949 | 49.7704 | 0.7563 | 75.1 | 2.8016
2024-01-06 07:00 | 0.6328 | 74.0526 | 49.804 | 0.7351 | 81.39 | 2.8016
2024-01-06 08:00 | 0.63937 | 74.0714 | 49.8495 | 0.77209 | 88.4 | 2.8016
2024-01-06 09:00 | 0.64142 | 74.0553 | 49.8937 | 0.82404 | 92.23 | 2.8016
2024-01-06 10:00 | 0.64004 | 74.0148 | 49.9292 | 0.97978 | 97.3 | 2.8016
2024-01-06 11:00 | 0.63655 | 73.9637 | 49.9547 | 1.1292 | 100.43 | 2.8016
2024-01-06 12:00 | 0.63209 | 73.914 | 49.9699 | 1.1776 | 99.16 | 2.8016
2024-01-06 13:00 | 0.62757 | 73.8745 | 49.9755 | 1.1179 | 95.22 | 2.8016
2024-01-06 14:00 | 0.62343 | 73.8485 | 49.9741 | 1.0019 | 92.55 | 2.8016
2024-01-06 15:00 | 0.62001 | 73.8379 | 49.9637 | 0.91292 | 95.09 | 2.8016
2024-01-06 16:00 | 0.61631 | 73.8357 | 49.9557 | 0.81233 | 99.85 | 2.8016
2024-01-06 17:00 | 0.61144 | 73.8368 | 49.9568 | 0.76366 | 104.27 | 2.8016
2024-01-06 18:00 | 0.60453 | 73.8353 | 49.9729 | 0.74544 | 103.63 | 2.8016
2024-01-06 19:00 | 0.59481 | 73.823 | 50.0046 | 0.78065 | 99 | 2.8016
2024-01-06 20:00 | 0.58152 | 73.7859 | 50.0488 | 0.82232 | 92.14 | 2.8016
2024-01-06 21:00 | 0.56447 | 73.7046 | 50.0972 | 0.85424 | 88 | 2.8016
2024-01-06 22:00 | 0.54615 | 73.5786 | 50.1483 | 0.83945 | 86.57 | 2.8016
2024-01-06 23:00 | 0.52928 | 73.4414 | 50.1871 | 0.78817 | 79.87 | 2.8016
2024-01-07 | 0.51478 | 73.3096 | 50.2042 | 0.67968 | 84.08 | 2.8016
2024-01-07 01:00 | 0.52204 | 73.3652 | 50.1169 | 0.49686 | 79.82 | 2.8016
2024-01-07 02:00 | 0.53611 | 73.4571 | 49.9774 | 0.35088 | 76.76 | 2.8016
2024-01-07 03:00 | 0.55582 | 73.5806 | 49.8288 | 0.16164 | 73.46 | 2.8016
2024-01-07 04:00 | 0.57854 | 73.7211 | 49.7081 | -0.0077127 | 71.86 | 2.8016
2024-01-07 05:00 | 0.60099 | 73.8583 | 49.6408 | -0.22216 | 72.08 | 2.8016
2024-01-07 06:00 | 0.62024 | 73.9753 | 49.6351 | -0.4379 | 74.9 | 2.8016
2024-01-07 07:00 | 0.63508 | 74.0633 | 49.6723 | -0.85538 | 77.69 | 2.8016
2024-01-07 08:00 | 0.64547 | 74.1201 | 49.7294 | -1.1508 | 81.79 | 2.8016
2024-01-07 09:00 | 0.65142 | 74.1468 | 49.7915 | -1.1978 | 84.86 | 2.8016
2024-01-07 10:00 | 0.65342 | 74.1459 | 49.8503 | -1.1318 | 87.15 | 2.8016
2024-01-07 11:00 | 0.65301 | 74.13 | 49.896 | -0.87866 | 89.14 | 2.8016
2024-01-07 12:00 | 0.6509 | 74.1103 | 49.9308 | -0.87273 | 88.66 | 2.8016
2024-01-07 13:00 | 0.64831 | 74.0973 | 49.9499 | -0.97483 | 84.81 | 2.8016
2024-01-07 14:00 | 0.64592 | 74.0958 | 49.9544 | -1.1553 | 84.34 | 2.8016
2024-01-07 15:00 | 0.64375 | 74.1074 | 49.9505 | -1.4787 | 88.01 | 2.8016
2024-01-07 16:00 | 0.64174 | 74.1321 | 49.9425 | -1.8178 | 93.42 | 2.8016
2024-01-07 17:00 | 0.63953 | 74.1684 | 49.9354 | -2.0307 | 101.77 | 2.8016
2024-01-07 18:00 | 0.6363 | 74.2137 | 49.9398 | -1.9628 | 104.85 | 2.8016
2024-01-07 19:00 | 0.63044 | 74.2512 | 49.9632 | -1.7533 | 103.55 | 2.8016
2024-01-07 20:00 | 0.62089 | 74.2596 | 49.9979 | -1.6042 | 100.5 | 2.8016
2024-01-07 21:00 | 0.60777 | 74.2175 | 50.03 | -1.4837 | 93.31 | 2.8016
2024-01-07 22:00 | 0.59343 | 74.1256 | 50.057 | -1.5083 | 91.17 | 2.8016
2024-01-07 23:00 | 0.58057 | 74.0139 | 50.0638 | -1.5528 | 83.86 | 2.8016

## Configuration
Parameter | Value
HEAT PUMP CONFIGURATION
Fixed Capacity | 0.6 MW
Type | Fenagy H600
Min Part Load | 30.0%
Startup Cost | 50 EUR
Min Uptime | 2 hours
Min Downtime | 1 hours
STORAGE CONFIGURATION
Temperature Supply | 70°C
Temperature Return | 40°C
Standing Loss | 2.0% per hour
Conversion Factor | 0.03488 MWh/m³
Cost Coefficient | 5551.7 EUR/m³
Cost Exponent | -0.35
Lifetime | 30 years
Discount Rate | 5.0%
OPTIMIZATION SETTINGS
MIP Gap | 20.0%
Time Limit | 3.0 minutes
Initial Guess | 250 m³/MW
Convergence Tolerance | 5.0%
Max Iterations | 10
PRICING
Use Spot Prices | Yes
Grid Electricity Price (fallback) | 80 EUR/MWh
Peak Boiler Cost | 120 EUR/MWh